SECTION 21 11 00

FIRE SPRINKLER FITTINGS AND VALVES

Display hidden notes to specifier. (Don't know how? Click Here) 
 Copyright 2018 -  2019 ARCAT, Inc. - All rights reserved

PART 1    GENERAL
1.1	SECTION INCLUDES
A.	Fire sprinkler fittings and valves including the following:
1.	Test and drain valves.
2.	Auxiliary drains.
3.	Corrosion monitor.
4.	Floor control risers.
5.	Inspectors test and drain valves.
6.	Test water containment system.
7.	Air venting valves.
8.	Accessories.
1.2	RELATED SECTIONS
A.	Section 22 05 00 - Common Work Results for Plumbing.
B.	Section15300 - Fire Protection Piping.
1.3	SUBMITTALS
A.	Submit under provisions of Section 01 30 00 - Administrative Requirements.
B.	Product Data:
1.	Manufacturer's data sheets on each product to be used.
2.	Preparation instructions and recommendations.
3.	Storage and handling requirements and recommendations.
4.	Typical installation methods.
C.	Verification Samples: For each finish product specified, two samples, minimum size 6 inches (150 mm) square representing actual product, color, and patterns.
D.	Shop Drawings: Include details of materials, construction and finish. Include relationship with adjacent construction. 
1.4	QUALITY ASSURANCE
A.	Manufacturer Qualifications: Company specializing in manufacturing products specified in this section with a minimum five years documented experience.
B.	Installer Qualifications: Company specializing in performing Work of this section with minimum two years documented experience with projects of similar scope and complexity.
C.	Source Limitations: Provide each type of product from a single manufacturing source to ensure uniformity.
D.	Mock-Up: Construct a mock-up with actual materials in sufficient time for Architect's review and to not delay construction progress. Locate mock-up as acceptable to Architect and provide temporary foundations and support.
1.	Intent of mock-up is to demonstrate quality of workmanship and visual appearance.
2.	If mock-up is not acceptable, rebuild mock-up until satisfactory results are achieved.
3.	Retain mock-up during construction as a standard for comparison with completed work. 
4.	Do not alter or remove mock-up until work is completed or removal is authorized.
1.5	PRE-INSTALLATION CONFERENCE
A.	Convene a conference approximately two weeks before scheduled commencement of the Work. Attendees shall include Architect, Contractor and trades involved. Agenda shall include schedule, responsibilities, critical path items and approvals.
1.6	DELIVERY, STORAGE, AND HANDLING
A.	Store and handle in strict compliance with manufacturer's written instructions and recommendations.
B.	Protect from damage due to weather, excessive temperature, and construction operations.
1.7	PROJECT CONDITIONS
A.	Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's recommended limits.
1.8	SEQUENCING
A.	Ensure that products of this section are supplied to affected trades in time to prevent interruption of construction progress.
1.9	WARRANTY
A.	Manufacturer's Warranty: Provide manufacturer's standard limited warranty.
PART 2    PRODUCTS
2.1	MANUFACTURERS
A.	Acceptable Manufacturer: AGF Manufacturing, Inc. , which is located at:<BR />100 Quaker Ln.<BR />Malvern, PA 19355 <BR />Tel: 610-240-4900<BR />Fax: 610-240-4906<BR />Email: request info (rpancoast@agfmfg.com);Web: https://agfmfg.com 
B.	Substitutions: Not permitted.
C.	Requests for substitutions will be considered in accordance with provisions of Section 01 60 00 - Product Requirements.
2.2	INSPECTORS TEST STATION VALVE
A.	Series: TESTanDRAIN as manufactured by AGF Manufacturing, Inc.
1.	The lightweight and compact Models shall be 300 PSI rated single-handle ball valve designed to provide both the test and express drain functions required for a wet fire sprinkler system.
a.	Standard: UL's "Product iQ" listing or "Approval Guide," published by FM Global, listing. NFPA 13, 13R, 13D (as applicable).
b.	Pressure Rating: 300 psig (2070 kPa).
c.	Materials: Bronze body, brass stem, impregnated Teflon seat, chrome coated brass ball, and a steel handle with positive stops at the TEST and DRAIN positions
d.	Components: A tamper resistant test orifice, integral tamper resistant sight glasses, a tapped and plugged port for system access, and a steel identification plate.
e.	Test Orifice Size: Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.
f.	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
g.	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
h.	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
i.	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition.
j.	Test Orifice Size: Nominal 14.0K (3/4 inch, ESFR), as required by NFPA 13, latest edition.
k.	Test Orifice Size: Nominal K25.2, as required by NFPA 13, latest edition.
l.	Size: Same as connected piping. 
m.	Inlet and Outlet: Threaded.
n.	Bypass drain port in the valve body for use with a pressure relief valve and associated drainage piping. 
2.	Product: Model M1000:
3.	Product: Model M1011 Type A with pressure relief valve.
a.	Pressure Relief Valve and Drainage Piping: AGF Model 7000
1)	Pressure Rating: Factory rated at 175 PSI. 
2)	Pressure Rating: 165 PSI.
3)	Pressure Rating: 185 PSI.
4)	Pressure Rating: 195 PSI.
5)	Pressure Rating: 205 PSI.
6)	Pressure Rating: 225 PSI.
7)	Pressure Rating: 250 PSI.
8)	Body Material: Bronze body and stainless steel spring
9)	Components: Nylobraid flexible tube, Two 1/2 inch (25 mm) NPT by barbed 90 degree elbows, external identification plate and integral flushing handle to remove debris
10)	1/2 inch (13 mm) MIPT inlet, 1/2 inch (13 mm) FIPT outlet
11)	Relief pressure shall be factory set to project specifications
12)	Relief valve shall operate to the OPEN position between 90 percent and 105 percent of the set pressure
13)	Relief valve shall reseat or CLOSE at a minimum of 80 percent of set pressure.
4.	Product: Model M1011 Type T with pressure relief valve and pressure gauge.
a.	Pressure Relief Valve and Drainage Piping: AGF Model 7000
1)	Pressure Rating: Factory rated at 175 PSI. 
2)	Pressure Rating: 165 PSI.
3)	Pressure Rating: 185 PSI.
4)	Pressure Rating: 195 PSI.
5)	Pressure Rating: 205 PSI.
6)	Pressure Rating: 225 PSI.
7)	Pressure Rating: 250 PSI.
8)	Body Material: Bronze body and stainless steel spring
9)	Components: Nylobraid flexible tube, Two 1/2 inch (25 mm) NPT by barbed 90 degree elbows, external identification plate and integral flushing handle to remove debris
10)	1/2 inch (13 mm)MIPT inlet, 1/2 inch (13 mm)FIPT outlet
11)	Relief pressure shall be factory set to project specifications
12)	Relief valve shall operate to the OPEN position between 90 percent and 105 percent of the set pressure
13)	Relief valve shall reseat or CLOSE at a minimum of 80 percent of set pressure.
b.	Pressure Gauge: AGF Model 7500.
c.	Globe Valve: AGF Model 7600.
B.	Series: TESTanDRAIN as manufactured by AGF Manufacturing, Inc.
1.	Standard: UL's "Product iQ" listing or "Approval Guide," published by FM Global, listing. NFPA 13, 13R, 13D (as applicable).
2.	Pressure Rating: 300 psig (2070 kPa).
3.	Materials: Bronze body, brass stem, impregnated Teflon seat, chrome coated brass ball, and a steel handle with positive stops at the TEST and DRAIN positions
4.	Components: A tamper resistant test orifice, integral tamper resistant sight glasses, a tapped and plugged port for system access, and a steel identification plate.
5.	Test Orifice Size: Nominal 2.8K (3/8 inch), as required by NFPA 13, latest edition.
6.	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
7.	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
8.	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
9.	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition.
10.	Test Orifice Size: Nominal 14.0K (3/4 inch, ESFR), as required by NFPA 13, latest edition.
11.	Test Orifice Size: Nominal K25.2, as required by NFPA 13, latest edition.
12.	Inlet and Outlet Size: 1 inch (25 mm) NPT.
13.	Inlet and Outlet Size: 1-1/4 inches (32 mm) NPT.
14.	Inlet and Outlet Size: 2 inches (51 mm) Groove.
15.	Bypass drain port in the valve body for use with a pressure relief valve and associated drainage piping.
16.	Product: Model M2500.
17.	Product: Model M2511. Type A with pressure relief valve. Section A.3. for the M1011 has several more details which should be included here. 
a.	Pressure Relief Valve and Drainage Piping: AGF Model 7000
1)	Pressure Rating: Factory rated at 175 PSI. 
2)	Pressure Rating: 165 PSI.
3)	Pressure Rating: 185 PSI.
4)	Pressure Rating: 195 PSI.
5)	Pressure Rating: 205 PSI.
6)	Pressure Rating: 225 PSI.
7)	Pressure Rating: 250 PSI.
8)	Body Material: Bronze body and stainless steel spring
9)	Components: Nylobraid flexible tube, Two 1/2 inch (25 mm) NPT by barbed 90 degree elbows, external identification plate and integral flushing handle to remove debris
10)	1/2 inch (13 mm) MIPT inlet, 1/2 inch (13 mm)FIPT outlet
11)	Relief pressure shall be factory set to project specifications
12)	Relief valve shall operate to the OPEN position between 90 percent and 105 percent of the set pressure
13)	Relief valve shall reseat or CLOSE at a minimum of 80 percent of set pressure.
18.	Product: Model M2511. Type T with pressure relief valve and pressure gauge.
a.	Pressure Relief Valve and Drainage Piping: AGF Model 7000
1)	Pressure Rating: Factory rated at 175 PSI. 
2)	Pressure Rating: 165 PSI.
3)	Pressure Rating: 185 PSI.
4)	Pressure Rating: 195 PSI.
5)	Pressure Rating: 205 PSI.
6)	Pressure Rating: 225 PSI.
7)	Pressure Rating: 250 PSI.
8)	Body Material: Bronze body and stainless steel spring
9)	Components: Nylobraid flexible tube, Two 1/2 inch (13 mm) NPT by barbed 90 degree elbows, external identification plate and integral flushing handle to remove debris.
10)	1/2 inch (13 mm) MIPT inlet, 1/2 inch (13 mm) FIPT outlet.
11)	Relief pressure shall be factory set to project specifications
12)	Relief valve shall operate to the OPEN position between 90 percent and 105 percent of the set pressure
13)	Relief valve shall reseat or CLOSE at a minimum of 80 percent of set pressure.
b.	Pressure Gauge: AGF Model 7500.
c.	Globe Valve: AGF Model 7600.
C.	Series: Remote Test Station as manufactured by AGF Manufacturing, Inc.
1.	Product: Model M1200 RemoteTEST 
a.	Standard: UL's "Product iQ" listing or "Approval Guide," published by FM Global, listing. NFPA 13, NFPA 13R, NFPA 13D, NFPA 70 and NFPA 72 (as applicable).
b.	Pressure Rating: 300 psig (2070 kPa).
c.	Body Material: Bronze body, brass stem, impregnated Teflon seat, chrome coated brass ball, and a steel handle with positive stops at the TEST and DRAIN positions
d.	Components: A tamper resistant test orifice, integral tamper resistant sight glasses, a tapped and plugged port for system access, and a steel identification plate.
e.	Test Orifice Size: Nominal 2.8K (3/8 inch), as required by NFPA 13, latest edition.
f.	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
g.	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
h.	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
i.	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition.
j.	Test Orifice Size: Nominal 14.0K (3/4 inch, ESFR), as required by NFPA 13, latest edition.
k.	Test Orifice Size: Nominal K25.2, as required by NFPA 13, latest edition.
l.	Size: Same as connected piping. Should have more detail like B.12, B.13 and B.14.
m.	Inlet and Outlet: Threaded.
n.	Solenoid Valve: 
1)	24V DC, or 120V AC.
2)	Pressure Rating: 300 psig (2070 kPa).
o.	Bypass Drain Loop: To connect the solenoid valve outlet to the bypass drain port.
D.	Series: Alarm Check Test Valve as manufactured by AGF Manufacturing, Inc.
1.	Construction:
a.	Standard: UL's "Procut iQ" listing or "Approval Guide," published by FM Global, listing. NFPA 13, 13R, 13D (as applicable).
b.	Pressure Rating: 300 psig (2070 kPa).
c.	Materials: Iron body, brass stem, impregnated Teflon seat, chrome coated brass ball, and a steel handle with positive stops at the TEST and DRAIN positions
d.	Components: A tamper resistant test orifice, a tapped and plugged port for system access, and a steel identification plate.
e.	Test Orifice Size: Nominal 2.8K (3/8 inch), as required by NFPA 13, latest edition.
f.	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
g.	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
h.	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
i.	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition.
j.	Test Orifice Size: Nominal 14.0K (3/4 inch, ESFR), as required by NFPA 13, latest edition.
k.	Test Orifice Size: Nominal K25.2, as required by NFPA 13, latest edition.
l.	Size: 2 inch BSPT.
m.	Inlet and Outlet: Threaded.
2.	Product: Model DRAINanTEST M1500.
3.	Product: Model DRAINanTEST M1511 with pressure relief valve and drainage piping AGF Model 7000.
a.	Pressure Rating: Factory rated at 175 PSI. 
b.	Pressure Rating: 165 PSI.
c.	Pressure Rating: 185 PSI.
d.	Pressure Rating: 195 PSI.
e.	Pressure Rating: 205 PSI.
f.	Pressure Rating: 225 PSI.
g.	Pressure Rating: 250 PSI.
h.	Body Material: Bronze body and stainless steel spring
i.	Components: Nylobraid flexible tube, Two 1/2 inch (25 mm) NPT by barbed 90 degree elbows, external identification plate and integral flushing handle to remove debris
j.	1/2 inch (13 mm) MIPT inlet, 1/2 inch (13 mm) FIPT outlet.
k.	Relief pressure shall be factory set to project specifications.
l.	Relief valve shall operate to the OPEN position between 90 percent and 105 percent of the set pressure.
m.	Relief valve shall reseat or CLOSE at a minimum of 80 percent of set pressure.
2.3	AUXILIARY DRAINS
A.	Series: COLLECTanDRAIN as manufactured by AGF Manufacturing, Inc.
1.	Product M5100. Easily accessed drain locations that collect small amounts of water over long durations of time.
a.	Standards: NFPA 13 and NFPA 25.
b.	Material: Galvanized Auxiliary Drain with Anti-Trip Plate and Water Detector.
c.	Material: Black Steel Pipe Auxiliary Drain with Anti-Trip Plate and Water Detector.
d.	Components:
1)	1 inch MIPT x FIPT Brass quarter turn ball valve with chrome plated ball.
2)	1 inch MIPT x FIPT Ball Valve with Side Ports.
3)	Water Detection Alarm with Brass Nipple.
a)	Powered by a 9-volt battery to operate a red LED visual indicator and an over 92 dB beeping alarm which are activated when water is present in the COLLECTanDRAIN.
b)	Battery operated system provides multiple years of service for intermittent alarming or can operate continuously for 72 hours. Unit will provide low battery power indication through audible chirp and yellow LED visual indicator.
c)	Device may be optionally hardwired to a 12 to 24 VDC power source.
d)	Unit features a test button to confirm operational integrity, offers left or right side installation, and can be isolated for service or battery replacement.
e)	Unit may be configured to alarm only when temperature is below 45 degreesF or at any temperature.
f)	Device may be wired to provide remote notification with NO and NC terminals.
4)	Anti-Trip Plate (ATP): Prevents the opening of either the upper or lower drain valve unless the opposite valve is in the correct closed position, preventing an accidental/malicious tripping of the alarm valve and filling of the sprinkler system.
a)	ATP is powder coated safety red for corrosion resistance and silk-screened with both "AUXILIARY DRAIN" and operating instructions.
b)	ATP can be locked to prevent tampering.
5)	Anti-Trip Plate Mounting Hardware Set.
6)	Two 1 inch by 2 inch (25 mm by 51 mm) Bell Reducer.
7)	2 inch by 12 inch long (51 mm by 305 mm) Condensate Nipple.
8)	1 inch (25 mm) Galvanized Square Head Plug.
e.	Model: Model M5100ALBV. Water Detector Alarm with Ball Valve.
f.	Model: Model M5150ALBV. Water Detector Alarm with Reversible Tee and Ball Valve. Minimum volume installation (1 oz.).
g.	Model: Model M5150ALBV. Water Detector Alarm with Reversible Tee and Ball Valve. Minimum volume installation (2 oz.).
2.	Product: Model 5200. Easily accessed drain locations that do not frequently collect water.
a.	Material: Galvanized Auxiliary Drain with Anti-Trip Plate.
b.	Material: Black Steel Pipe Auxiliary Drain with Anti-Trip Plate.
c.	Standards:
1)	UL's "Product iQ" listing or "Approval Guide," published by FM Global, listing.
2)	NFPA 13 and NFPA 25.
d.	Components:
1)	Two1 inch (13 mm) MIPT x FIPT Brass quarter turn ball valves with chrome plated balls.
2)	Anti-Trip Plate (ATP): Prevents the opening of either the upper or lower drain valve unless the opposite valve is in the correct closed position, preventing an accidental/malicious tripping of the alarm valve and filling of the sprinkler system.
a)	ATP is powder coated safety red for corrosion resistance and silk-screened with both "AUXILIARY DRAIN" and operating instructions.
b)	ATP can be locked to prevent tampering.
3)	Anti-Trip Plate Mounting Hardware Set.
4)	Two 1 inch by 2 inch (25 mm by 51 mm) Bell Reducers.
5)	2 inch by 12 inch long (51 mm by 305 mm) Condensate Nipple.
6)	1 inch (15 mm) Galvanized Square Head Plug.
3.	Product: M5300.
a.	Type A: Galvanized Auxiliary Drain.
b.	Type B: Black Steel Pipe Auxiliary Drain.
c.	Type ALBV: Galvanized Auxiliary Drain with Water Detector.
d.	Type ALBV-B: Black Steel Pipe Auxiliary Drain with Water Detector.
e.	Standards:
1)	UL's "Product iQ" listing or "Approval Guide," published by FM Global, listing.
2)	NFPA 13 and NFPA 25.
f.	Components:
1)	Two 1 inch (25 mm) MIPT x FIPT Brass quarter turn ball valves with chrome plated balls.
2)	Two 1 inch by 2 inch (25 mm by 51 mm) Bell Reducers.
3)	2 inch by 12 inch long (51 mm by 305 mm) Condensate Nipple.
4)	1 inch (25 mm) Galvanized Square Head Plug.
B.	Series: Heated and Insulated Cabinet as manufactured by AGF Manufacturing, Inc.:
1.	Standards: NFPA 13 and NFPA 25.
2.	Components:
a.	Cabinet: A secure locking, red powder coated, insulated cabinet with required signage adhering to NFPA guidelines.
b.	Heating Element: Temperature sensitive internal heating element to prevent excess condensation in the drum drip from freezing.
c.	Float Switch: Activates an audible alarm and visual signal to notify when the auxiliary drain has reached capacity and the drum drip requires draining.
d.	System Alarm Test Button: An integral TEST button allows for system testing.
e.	Thermometer: Externally mounted for easy monitoring of temperature conditions inside the cabinet.
f.	Drain Assembly:
1)	Two 1 inch by 2 inch (25 mm by 51 mm) Bell Reducers.
2)	2 inch by 12 inch long (51 mm by 305 mm) Condensate Nipple.
3)	1 inch (25 mm) Galvanized Square Head Plug.
4)	Two 1 inch (25 mm) MIPT x FIPT Brass quarter turn ball valves with chrome plated balls.
5)	Mounting hardware.
6)	Each unit is fully assembled and ready to be attached to dry pipe systems using galvanized or black piping components and 1-inch brass quarter turn ball valves with chrome plated brass balls.
3.	Product: Model 5400A. Cabinet with Galvanized Auxiliary Drain and Heater.
4.	Product: Model 5400B. Cabinet with Black Steel Pipe Auxiliary Drain and Heater.
5.	Product: Model 5400H. Cabinet with Hot Operation Trouble Monitor.
6.	Product: Model 5400D. Cabinet with Remote Dialer.
7.	Product: Model 5580A. All-Weather Cover.
2.4	CORROSION MONITOR
A.	Series: CORRinSITE as manufactured by AGF Manufacturing, Inc.
1.	Product: Model 7700. 
a.	Standards:
1)	NFPA 13 and NFPA 25.
b.	Specifications:
1)	Service Pressure: 300 PSI.
2)	Operating Temp.: -40 degrees to 200 degrees F.
3)	Material: Mild Carbon Steel.
4)	Wear Dimension: 0.040 inch.
5)	Sizes: 2 inches.
6)	Sizes: 2-1/2 inches.
7)	Sizes: 3 inches.
8)	Sizes: 4 inches.
9)	Sizes: 6 inches.
10)	Sizes: 8 inches.
11)	Schedule 10.
12)	Schedule 40.
13)	For Black and Galvanized Pipe.
c.	Finish: Powder-coat. Color - Red.
d.	Finish: Hot-dip galvanized.
2.	Product: Model 7800.
a.	Standards: NFPA 13 and NFPA 25.
b.	Specifications:
1)	Service Pressure: 300 PSI.
2)	Operating Temp.: -40 degree to 200 degree F.
3)	Material: Mild Carbon Steel.
4)	Wear Dimension: 0.040 inch (1 mm).
5)	Sizes: 2 inches (51 mm).
6)	Sizes: 2-1/2 inches (64 mm).
7)	Sizes: 3 inches (76 mm).
8)	Sizes: 4 inches (102 mm).
9)	Sizes: 6 inches (152 mm).
10)	Sizes: 8 inches (203 mm).
11)	NOT APPLICABLE FOR 7800 NOT APPLICABLE FOR 7800For Black and Galvanized Pipe.
c.	Finish: Powder-coat. Color - Red.
d.	Finish: Hot-dip galvanized.
2.5	FLOOR CONTROL RISERS
A.	Series: RiserPACK as manufactured by AGF Manufacturing, Inc.
B.	Product: Residential Model M8000 13R. Includes a flow switch, InspectorsTEST Model 3011BV, 3-way globe valve, and a M7500 pressure gauge.
1.	Pre-Assembled TESTanDRAIN Riser:
a.	One-piece bronze casting, lettered on both sides allowing right or left installation and providing required signage for flow direction, test and drain outlet, and gauge location. 
b.	Standards: 
1)	UL's "Product iQ" listing or "Approval Guide," published by FM Global, listing.
2)	NFPA 13R, 13D.
c.	Pressure Rating: 300 psig (2070 kPa).
d.	Test Orifice Size 1 inch (25 mm) Model: 
1)	Test Orifice Size: Nominal 2.8K (3/8 inch), as required by NFPA 13, latest edition.
2)	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
3)	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
e.	Test Orifice Size 1-1/4, 1-1/2, and 2 inches (32 mm, 38 mm, 51 mm) Models.
1)	Test Orifice Size: Nominal 2.8 K (3/8 inch), as required by NFPA 13, latest edition.
2)	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
3)	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
4)	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
5)	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition.
f.	Size: Same as connected piping.
g.	Inlet and Outlet: Threaded.
h.	Inlet and Outlet: Grooved 1-1/2 to 2 inches (38 mm to 51 mm).
i.	Inlet and Outlet: Threaded and Grooved 1-1/2 to 2 inches (38 mm to 51 mm).
j.	3/4 inch Male x Female ball valve 1 inch (25 mm) Model: Orifice specific outlet designed to accept either a standard garden hose or hard piped drain outlet.
k.	AGF Model 3011BV Inspector's TEST ball valve 1-1/4, 1-1/2, and 2 inch (32 mm, 38 mm, 51 mm) Models.
l.	Water flow alarm switch.
m.	Pressure Gauge: AGF Model 7500.
C.	Product: Residential Model M8000 13D. Includes a flow switch, InspectorsTEST Model 3011A and M7500 Pressure Gauge,
1.	Pre-Assembled TESTanDRAIN Riser:
a.	One-piece bronze casting, lettered on both sides allowing right or left installation and providing required signage for flow direction, test and drain outlet, and gauge location. AVAILABLE PIPE SIZES?
b.	Standard: UL's "Product iQ" listing or "Approval Guide," published by FM Global, listing. NFPA 13R, 13D.
c.	Pressure Rating: 300 psig (2070 kPa).
d.	Model Test Orifice Size 1 inches (25 mm) Model: 
1)	Test Orifice Size: Nominal 2.8K (3/8 inch), as required by NFPA 13, latest edition.
2)	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
3)	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
e.	Model Test Orifice Size 1-1/4, 1-1/2, and 2 inch (32 mm, 38 mm, 51 mm) Models: 
1)	Test Orifice Size: Nominal 2.8K (3/8 inch), as required by NFPA 13, latest edition.
2)	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
3)	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
4)	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
5)	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition.
f.	Size: Same as connected piping.
g.	Inlet and Outlet: Threaded.
h.	Inlet and Outlet: Grooved 1-1/2 to 2 inches (38 mm to 51 mm).
i.	Inlet and Outlet: Threaded and Grooved 1-1/2 to 2 inches (38 mm to 51 mm).
j.	3/4 inch (19 mm) Male x Female ball valve (1 inch (25 mm) Model): Orifice specific outlet designed to accept either a standard garden hose or hard piped drain outlet.
k.	Model 3011BV Inspector's TEST ball valve (1-1/4, 1-1/2, and 2 inches (32 mm, 38 mm, and 52 mm) Models).
l.	Water flow alarm switch.
m.	Pressure Gauge: AGF Model 7500.
D.	Product: Residential Model M8011 13D. Includes a flow switch, InspectorsTEST Model 3011A, M7500 Pressure Gauge, and a Model 7200 Pressure Relief Valve. 
1.	Pre-Assembled TESTanDRAIN Riser:
a.	One-piece bronze casting, lettered on both sides allowing right or left installation and providing required signage for flow direction, test and drain outlet, and gauge location.
b.	Standard: UL's "Product iQ" listing or "Approval Guide," published by FM Global, listing. NFPA 13R, 13D.
c.	Pressure Rating: 300 psig (2070 kPa).
d.	Model Test Orifice Size 1 inches (25 mm) Model: 
1)	Test Orifice Size: Nominal 2.8K (3/8 inch), as required by NFPA 13, latest edition.
2)	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
3)	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
e.	Model Test Orifice Size 1-1/4, 1-1/2, and 2 inch (32 mm, 38 mm, 51 mm) Models: 
1)	Test Orifice Size: Nominal 2.8K (3/8 inch), as required by NFPA 13, latest edition.
2)	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
3)	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
4)	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
5)	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition.
f.	Size: Same as connected piping.
g.	Inlet and Outlet: Threaded.
h.	Inlet and Outlet: Grooved 1-1/2 to 2 inches (38 mm to 51 mm).
i.	Inlet and Outlet: Threaded and Grooved 1-1/2 to 2 inches (38 mm to 51 mm).
j.	3/4 inch (19 mm) Male x Female ball valve (1 inch (25 mm) Model): Orifice specific outlet designed to accept either a standard garden hose or hard piped drain outlet.
k.	Model 3011BV Inspector's TEST ball valve (1-1/4, 1-1/2, and 2 inches (32 mm, 38 mm, and 52 mm) Models).
l.	Water flow alarm switch.
m.	Pressure Gauge: AGF Model 7500.
n.	Pressure Relief Valve and Drainage Piping: Model 7000.
1)	Pressure Rating: Factory rated at 175 PSI. 
2)	Pressure Rating: 165 PSI.
3)	Pressure Rating: 185 PSI.
4)	Pressure Rating: 195 PSI.
5)	Pressure Rating: 205 PSI.
6)	Pressure Rating: 225 PSI.
7)	Pressure Rating: 250 PSI.
o.	Body Material: Bronze body and stainless steel spring
p.	Components: Nylobraid flexible tube, One 1/2 inch (13 mm) NPT by barbed 90 degree elbow, one 1/2 inch (13mm) NPT by barbed straight adapter, external identification plate and integral flushing handle to remove debris
q.	1/2 inch (13 mm) MIPT inlet, 1/2 inch (13 mm) FIPT outlet.
r.	Relief pressure shall be factory set to project specifications.
s.	Relief valve shall operate to the OPEN position between 90 percent and 105 percent of the set pressure.
E.	Product: Residential Model M8011 13R. Includes a flow switch, InspectorsTEST Model 3011A, Model 7600 3-way Globe Valve, M7500 Pressure Gauge, and a Model 7000 Pressure Relief Valve.
1.	Pre-Assembled TESTanDRAIN Riser:
a.	One-piece bronze casting, lettered on both sides allowing right or left installation and providing required signage for flow direction, test and drain outlet, and gauge location. 
b.	Standard: UL's "Product iQ" listing or "Approval Guide," published by FM Global, listing. NFPA 13R, 13D.
c.	Pressure Rating: 300 psig (2070 kPa).
d.	Test Orifice Size: Nominal 2.8K (3/8 inch), as required by NFPA 13, latest edition.
e.	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
f.	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
g.	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
h.	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition.
i.	Size: Same as connected piping.
j.	Inlet and Outlet: Threaded 1-1/4 to 2 inches (32 mm to 51 mm)
k.	Inlet and Outlet: Grooved 1-1/2 to 2 inches (38 mm to 51 mm).
l.	Inlet and Outlet: Threaded and Grooved 1-1/2 to 2 inches (38 mm to 51 mm).
m.	Model 3011BV Inspector's TEST ball.
n.	Water flow alarm switch.
o.	Pressure Gauge: AGF Model 7500.
p.	Globe Valve: AGF Model 7600, 1/4 inch 3 mm) 3-way globe valve.
q.	Pressure Relief Valve and Drainage Piping 1-1/4 to 2 inches (32 to 51 mm) Model: AGF Model 7000.
r.	Pressure Rating: Factory rated at 175 PSI. 
s.	Pressure Rating: 165 PSI.
t.	Pressure Rating: 185 PSI.
u.	Pressure Rating: 195 PSI.
v.	Pressure Rating: 205 PSI.
w.	Pressure Rating: 225 PSI.
x.	Pressure Rating: 250 PSI.
y.	Body Material: Bronze body and stainless steel spring.
z.	Components: Nylobraid flexible tube, One 1/2 inch (13 mm) NPT by barbed 90 degree elbow, one 1/2 inch (13 mm) NPT by barbed straight adapter, external identification plate and integral flushing handle to remove debris.
aa.	1/2 inch (13 mm) MIPT inlet, 1/2 inch (13 mm) FIPT outlet.
ab.	Relief pressure shall be factory set to project specifications.
ac.	Relief valve shall operate to the OPEN position between 90 percent and 105 percent of the set pressure.
ad.	Relief valve shall reseat or CLOSE at a minimum of 80 percent of set pressure.
F.	Product: Commercial Model M8000. Includes a flow switch, TESTanDRAIN Model 2500, Model 7600 3-way Globe Valve, and a M7500 Pressure Gauge.
1.	Riser Model: Pre-Assembled TESTanDRAIN Riser 1-1/4, 1-1/2. and 2 inches (32 mm, 38 mm, 51 mm):
a.	One-piece bronze casting, lettered on both sides allowing right or left side draining, horizontal or vertical installation.
b.	Inlet and Outlet (Cast bronze):
1)	Inlet and Outlet: Threaded.
2)	Inlet and Outlet: Grooved 1-1/2 to 2 inches (38 mm to 51 mm).
3)	Inlet and Outlet: Threaded and Grooved 1-1/2 to 2 inches (38 mm to 51 mm).
c.	Standard: UL's "Product iQ" listing, or "Approval Guide," published by FM Global, listing. NFPA 13.
d.	Pressure Rating: 300 psig (2070 kPa).
e.	Size: Same as connected piping.
2.	Riser Model: Pre-Assembled TESTanDRAIN Riser 2-1/2, 3, 4, and 6 inch (64 mm, 76 mm, 102 mm, 152 mm):
a.	Schedule 40 fabricated steel body with 3mil powder coated red finish.
b.	Inlet and Outlet (Schedule 40 steel):
1)	Inlet and Outlet: Grooved 2-1/2, 3, 4 and 6 inches (64 mm, 76 mm, 102 mm, 152 mm) Models.
c.	Standard: UL's "Product iQ" listing, or "Approval Guide," published by FM Global, listing. NFPA 13.
d.	Pressure Rating: 300 psig (2070 kPa).
e.	Size: Same as connected piping.
3.	Valve Model 2500 TESTanDRAIN valve 1-1/4, 1-1/2, and 2 inch (32 mm, 28 mm, 51 mm) Models:
a.	1 inch (25 mm) FNPT.
b.	Test Orifice Size: Nominal 2.8K (3/8 inch), as required by NFPA 13, latest edition.
c.	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
d.	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
e.	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
f.	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition.
4.	Valve Model 2500 TESTanDRAIN valve 2-1/2 and 3 inches (38 mm, 76 mm) Models:
a.	1-1/4 inches (32 mm) FNPT.
b.	Test Orifice Size: Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.
c.	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
d.	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
e.	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
f.	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition.
g.	Test Orifice Size: Nominal 14.0K (3/4 inch, ESFR), as required by NFPA 13, latest edition.
h.	Test Orifice Size: Nominal K25.2, as required by NFPA 13, latest edition.
5.	Valve Model 2500 TESTanDRAIN valve 4 and 6 inches (102 mm, 152 mm) Models:
a.	2 inches (51 mm) Grooved.
b.	Test Orifice Size: Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.
c.	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
d.	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
e.	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
f.	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition.
g.	Test Orifice Size: Nominal 14.0K (3/4 inch, ESFR), as required by NFPA 13, latest edition.
h.	Test Orifice Size: Nominal K25.2, as required by NFPA 13, latest edition.
i.	Water flow alarm switch.
j.	Pressure Gauge: AGF Model 7500.
k.	1/4 inch (6 mm), 3-way globe valve: AGF Model 7600.
G.	Product: Commercial Model M8011. Includes a flow switch, TESTanDRAIN Model 2511A, Model 7600 3-way Globe Valve, and a M7500 Pressure Gauge and a model M7000 Pressure Relief Valve.
1.	Riser Model: Pre-Assembled TESTanDRAIN Riser 1-1/4, 1-1/2. and 2 inches (32 mm, 38 mm, 51 mm):
a.	One-piece bronze casting, lettered on both sides allowing right or left side draining, horizontal or vertical installation.
b.	Inlet and Outlet: Threaded.
c.	Inlet and Outlet: Grooved 1-1/2 to 2 inches (38 mm to 51 mm).
d.	Inlet and Outlet: Threaded and Grooved 1-1/2 to 2 inches (38 mm to 51 mm).
e.	Standard: UL's "Product iQ" listing, or "Approval Guide," published by FM Global, listing. NFPA 13.
f.	Pressure Rating: 300 psig (2070 kPa).
g.	Size: Same as connected piping.
2.	Riser Model: Pre-Assembled TESTanDRAIN Riser 2-1/2, 3, 4, and 6 inches (64 mm, 76 mm, 102 mm, 152 mm):
a.	Inlet and Outlet (Schedule 40 steel): Grooved 2-1/2, 3, 4 and 6 inches (64 mm, 76 mm, 102 mm, 152 mm) Models.
b.	Schedule 40 fabricated steel body with 3mil (.08 mm) powder coated red finish.
c.	Standard: UL's "Product iQ" listing, or "Approval Guide," published by FM Global, listing. NFPA 13.
d.	Pressure Rating: 300 psig (2070 kPa).
e.	Size: Same as connected piping.
3.	Valve Model 2511 TESTanDRAIN valve 1-1/4, 1-1/2, and 2 inch (32 mm, 38 mm, 51 mm) Models:
a.	1 inch (25 mm) FNPT.
b.	Test Orifice Size: Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.
c.	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
d.	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
e.	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
f.	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition
4.	Valve Model 2511 TESTanDRAIN valve 2-1/2 and 3 inches (64 mm, 76 mm) Models:
a.	1-1/4 inch FNPT.
b.	Test Orifice Size: Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.
c.	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
d.	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
e.	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
f.	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition.
g.	Test Orifice Size: Nominal 14.0K (3/4 inch, ESFR), as required by NFPA 13, latest edition.
5.	Valve Model 2511 TESTanDRAIN valve 4 and 6 inches (102 mm, 152 mm) Models:
a.	2 inch Grooved.
b.	Test Orifice Size: Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.
c.	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
d.	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
e.	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
f.	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition.
g.	Test Orifice Size: Nominal 14.0K (3/4 inch, ESFR), as required by NFPA 13, latest edition.
h.	Test Orifice Size: Nominal K25.2, as required by NFPA 13, latest edition.
6.	Water flow alarm switch.
7.	Pressure Gauge: AGF Model 7500.
8.	1/4 inch, 3-way globe valve: AGF Model 7600
9.	Pressure Relief Valve and Drainage Piping: AGF Model 7000
a.	Pressure Rating: Factory rated at 175 PSI. 
b.	Pressure Rating: 165 PSI.
c.	Pressure Rating: 185 PSI.
d.	Pressure Rating: 195 PSI.
e.	Pressure Rating: 205 PSI.
f.	Pressure Rating: 225 PSI.
g.	Pressure Rating: 250 PSI.
h.	Body Material: Bronze body and stainless steel spring.
i.	Components: Nylobraid flexible tube, Two 1/2 inch (13 mm) NPT by barbed 90 degree elbows, external identification plate and integral flushing handle to remove debris.
j.	1/2 inch (13 mm) MIPT inlet, 1/2 inch (13 mm) FIPT outlet.
k.	Relief pressure shall be factory set to project specifications.
l.	Relief valve shall operate to the OPEN position between 90 percent and 105 percent of the set pressure.
m.	Relief valve shall reseat or CLOSE at a minimum of 80 percent of set pressure.
2.6	INSPECTORS TEST VALVES
A.	Standards/Ratings:
1.	Standard: UL's "Product iQ" listing or "Approval Guide," published by FM Global, listing. NFPA 13, 13R, 13D as applicable.
2.	Pressure Rating: 300 psig (2070 kPa).
3.	Components: A tamper resistant test orifice and a tapped port for system access.
4.	Size: F.I.P.T., same as connected piping.
5.	Inlet and Outlet: Threaded.
6.	Test Orifice Size: Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.
7.	Test Orifice Size: Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.
8.	Test Orifice Size: Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.
9.	Test Orifice Size: Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.
10.	Test Orifice Size: Nominal 11.2K (5/8 inch, ELO), as required by NFPA 13, latest edition.
B.	Product: Model M3011BV. Inspector's Test Ball Valve. A 300 PSI rated ball valve designed to perform the remote inspector's test function on single story and other applications with the benefit of locating the orifice indoors.
1.	Body Material: Bronze body, brass stem, steel handle, chrome-plated bronze ball, virgin Teflon valve seat.
C.	Product: Model M3011A Inspector's Test with Pressure Relief Valve. includes a Model 7000 Pressure Relief Valve and drainage piping and complies with the requirements of NFPA 13 for the installation of a pressure relief valve on all gridded systems and downstream of all pressure reducing valves.
1.	Body Material: Bronze body, brass stem, steel handle, chrome-plated bronze ball, virgin Teflon valve seat.
2.	Pressure Relief Valve and Drainage Piping: Model 7000.
a.	Pressure Rating: Factory rated at 175 PSI. 
b.	Pressure Rating: 165 PSI.
c.	Pressure Rating: 185 PSI.
d.	Pressure Rating: 195 PSI.
e.	Pressure Rating: 205 PSI.
f.	Pressure Rating: 225 PSI.
g.	Pressure Rating: 250 PSI.
3.	Body Material: Bronze body and stainless steel spring
4.	Components: Nylobraid flexible tube, One 1/2 inch (13 mm) NPT by barbed 90 degree elbow, one 1/2 inch (13mm) NPT by barbed straight adapter, external identification plate and integral flushing handle to remove debris
5.	1/2 inch (13 mm) MIPT inlet, 1/2 inch (13 mm) FIPT outlet.
6.	Relief pressure shall be factory set to project specifications.
7.	Relief valve shall operate to the OPEN position between 90 percent and 105 percent of the set pressure.
8.	Relief valve shall reseat or CLOSE at a minimum of 80 percent of set pressure.
D.	Product: Model M3011SG Inspector's Test with Sight Glass. A 300 PSI rated ball valve designed to perform the remote inspector's test function on single story and other applications with the benefit of locating the orifice indoors.
1.	Body Material: Bronze body, brass stem, steel handle, chrome-plated bronze ball, virgin Teflon valve seat. Sight Glass: Bronze housing with viewing window.
E.	Product: Model M3011ASG Inspector's Test with Sight Glass and Pressure Relief Valve. Includes a sight glass as well as a Model 7000 Pressure Relief Valve with drainage piping and complies with the requirements of NFPA 13 for the installation of a pressure relief valve on all gridded systems and downstream of all pressure reducing valves.
1.	Body Material: Bronze body, brass stem, steel handle, chrome-plated bronze ball, virgin Teflon valve seat. Sight Glass: Bronze housing with viewing window.
2.	Pressure Relief Valve and Drainage Piping: AGF Model 7000
a.	Pressure Rating: Factory rated at 175 PSI. 
b.	Pressure Rating: 165 PSI.
c.	Pressure Rating: 185 PSI.
d.	Pressure Rating: 195 PSI.
e.	Pressure Rating: 205 PSI.
f.	Pressure Rating: 225 PSI.
g.	Pressure Rating: 250 PSI.
3.	Body Material: Bronze body and stainless steel spring.
4.	Components: Nylobraid flexible tube, One 1/2 inch (13 mm) NPT by barbed 90 degree elbow, one 1/2 inch (13 mm) NPT by barbed straight adapter, external identification plate and integral flushing handle to remove debris
5.	1/2 inch (13 mm) MIPT inlet, 1/2 inch (13 mm) FIPT outlet.
6.	Relief pressure shall be factory set to project specifications.
7.	Relief valve shall operate to the OPEN position between 90 percent and 105 percent of the set pressure.
8.	Relief valve shall reseat or CLOSE at a minimum of 80 percent of set pressure.
2.7	TEST WATER CONTAINMENT SYSTEM
A.	Product: TESTanSAVE as manufactured by AGF Manufacturing, Inc.
B.	Procedure: TESTanSAVE recirculates the sprinkler system test water back through the supply riser eliminating the need to reintroduce new water into the sprinkler system during testing. Its three step process is simple. First, water is brought in to perform the inspector's test on the first floor. Next, instead of water being drained to the outside, test water is recirculated into the system through the TESTanSAVE. Then, the recirculated water is used to perform the inspector's test on all of the additional floors.
2.8	AIR VENTING VALVES
A.	Series: PURGEnVENT as manufactured by AGF Manufacturing, Inc.
1.	Product: Model M7910MAV. Manual Air Venting Valve is a 1/2 inch (13 mm) ball valve with a mesh strainer and ball float.
a.	Standard: UL's "Product iQ" . NFPA 13, 13R, 13D (as applicable).
b.	Pressure Rating: 300 psig (2070 kPa).
c.	Body Material: Forged brass body.
d.	Components: Stainless steel inlet screen (60 mesh), polypropylene float, 
e.	Inlet Size: 1/2 inch (13 mm) NPT.
f.	Outlet Size: 1/2 inch (13 mm) NPT.
2.	Product: M7900AAV Automatically Vent Air from the System. Automatic Air Venting Valve is a 1 inch (25 mm) ball valve, strainer, air vent, and purge assembly.
a.	Standard: UL's "Product iQ" listing or "Approval Guide," published by FM Global, listing. NFPA 13, 13R, 13D (as applicable).
b.	Pressure Rating: 300 psig (2070 kPa), 175 psi (1205 kPa) for air vent.
c.	Body Material: Forged brass body.
d.	Components: Integrated ball valve, stainless steel strainer, purge valve with hose connection (Field adjustable), thread cap with lanyard, automatic air vent.
e.	Inlet Size: 1 inch NPT.
f.	Outlet Size: 3/4 inch (19 mm) NPT.
g.	Optional Water Collection Accessories:
1)	Product: Model 7920AI. Water Collection Assembly with Audible Alarm.
2)	Product: Model 7925VI. Water Collection Assembly with Visual Indicator.
3.	Product: M7930ECA Automatic Air Venting Valve with End Cap. The Model 7930ECA includes an end cap so it is easily installed onto the end of branch lines with a coupling.
a.	Standard: UL's "Fire Protection Equipment Directory" listing or "Approval Guide," published by FM Global, listing. NFPA 13, 13R, 13D (as applicable).
b.	Includes M7900AAV. 
c.	Pressure Rating: 300 psig (2070 kPa).
d.	End Cap: Painted, Ductile Iron with Groove end and 1" NPT offset connection.
e.	Inlet Size: 
1)	2 inches (51 mm) Grooved end.
2)	2.5 inches (64 mm) Grooved end.
3)	3 inches (76 mm) Grooved end.
4)	4 inches (102 mm) Grooved end.
5)	6 inches (152 mm) Grooved end.
6)	8 inches (203 mm) Grooved end.
f.	Optional Water Collection Accessories:
1)	Product: Model 7920AI. Water Collection Assembly with Audible Alarm.
2)	Product: Model 7925VI. Water Collection Assembly with Visual Indicator.
4.	Product: M7950ILV In-Line Automatic Air Venting Valve. The separation chamber and air scoop is designed to force a separation of air from the water as the system fills.
a.	Standard: UL's "Fire Protection Equipment Directory" listing or "Approval Guide," published by FM Global, listing. NFPA 13, 13R, 13D (as applicable).
b.	Includes M7900AAV. 
c.	Pressure Rating: 300 psig (2070 kPa).
d.	Separation Chamber: Carbon steel body with threaded fitting for machined brass Air Scoop attachment. Powder coated Safety Red.
e.	Inlet and Outlet Size: 2 inches (51 mm) Grooved ends.
f.	Inlet and Outlet Size: 2.5 inches (64 mm) Grooved ends.
g.	Inlet and Outlet Size: 3 inches (76 mm) Grooved ends.
h.	Inlet and Outlet Size: 4 inches (102 mm) Grooved ends.
i.	Inlet and Outlet Size: 6 inches (152 mm) Grooved ends.
j.	Inlet and Outlet Size: 8 inches (203 mm) Grooved ends.
k.	Optional Water Collection Accessories:
1)	Product: Model 7920AI. Water Collection Assembly with Audible Alarm.
2)	Product: Model 7925VI. Water Collection Assembly with Visual Indicator.
2.9	ACCESSORIES
A.	Smartgauge Pressure Gauge With Drag Needle:
1.	Product: Model SMARTGAUGE Model 7550. A 4 inches (102 mm) pressure gauge with a drag pointer designed to record system pressure spikes caused by municipal water supplies or pumps that are not working properly. Installed on a wet system temporarily or permanently to record pressure spikes so pressure relief valves can be sized correctly.
2.	Accuracy: Plus or minus 1 percent full scale.
3.	Pressure Gauge Range: 0-400 PSI (outside), 0-2740 kPa (inside)
4.	Connection: Brass, 1/4" (6 mm) NPT, Bottom
B.	Pressure Gauge:
1.	Product: Model 7500. 
2.	The pressure gauge is a UL Listed/FM Approved 4 inches (102 mm) pressure gauge designed for use on wet fire sprinkler systems. Designed to meet NFPA 13 requirements (2007 Edition) 7.1.1.1 - 7.1.1.2, 7.2.1 - 7.3.1.3, 7.8.7, 8.16.1.2.2, and 8.17.3. The AGF 1/4 inch (6 mm) 3-Way Globe Valve Model 7600 is designed to connect the pressure gauge to the sprinkler systems. The Model 7600 is designed to meet NFPA 13 System Attachments stating "...each gauge shall be equipped with a shutoff valve and provision for drainage". 1/4 inch (6 mm) Steel Plug not included.
3.	Standard: UL 393. NFPA 13, 13R, 13D (as applicable).
4.	Dial Size: 3-1/2 inches.
5.	Pressure Gauge Range: 0-300 PSI (Inside), 0-2000 kPa (Outside).
6.	Water System Piping Gauge: Include "WATER" label on dial face.
7.	Accuracy: Plus or minus 3-2-3 percent.
8.	Components:
a.	Burdon Tube: Phosphor Bronze.
b.	Window: Polycarbonate one-piece ring and crystal.
c.	Dial: Galvalume.
d.	Pointer: Aluminum, painted black.
e.	Case: PGE XenoyDX2735.
f.	Connection: Brass, 1/4 inch (6 mm) ANPT LM.
C.	Pressure Relief Valves:
1.	Product: Model 7000 Pressure Relief Valve. Designed to relieve excess pressure caused by pressure surges or temperature changes in all wet fire sprinkler systems.
a.	Standard: UL's "Product iQ" listing or "Approval Guide," published by FM Global, listing. NFPA 13, 13R, 13D (as applicable).
b.	Pressure Rating: Factory rated at 175 PSI. 
c.	Pressure Rating: 165 PSI.
d.	Pressure Rating: 185 PSI.
e.	Pressure Rating: 195 PSI.
f.	Pressure Rating: 205 PSI.
g.	Pressure Rating: 225 PSI.
h.	Pressure Rating: 250 PSI.
i.	Body Material: Bronze body and stainless steel spring.
j.	Components: External identification plate and integral flushing handle to remove debris
k.	1/2 inch (13 mm) MIPT inlet, 1/2 inch (13 mm) FIPT outlet.
l.	Relief pressure shall be factory set to project specifications.
m.	Relief valve shall operate to the OPEN position between 90 percent and 105 percent of the set pressure.
n.	Relief valve shall reseat or CLOSE at a minimum of 80 percent of set pressure. 
2.	Product: Model 7200 Pressure Relief Valve. Designed to provide the relief, test, and drain functions in a single valve.
a.	Standard: UL's "Product iQ" listing or "Approval Guide," published by FM Global, listing. NFPA 13, 13R, 13D (as applicable).
b.	Pressure Rating: Factory rated at 175 PSI. 
c.	Relief pressure shall be factory set to project specifications
d.	Body Material: Bronze body and stainless steel spring.
e.	Components: External identification plate and integral flushing handle to remove debris.
f.	3/4 inch MIPT inlet, 3/4 inch (19 mm) FIPT outlet.
g.	Relief valve shall operate to the OPEN position between 90 percent and 105 percent of the set pressure
h.	Relief valve shall reseat or CLOSE at a minimum of 80 percent of set pressure.
D.	Globe Valve:
1.	Product; Model 7600 Globe valve as manufactured by AGF Manufacturing, Inc.
2.	Standard: UL's "Product iQ" listing. Conforms to NFPA standards NFPA-13, NFPA-13R and NFPA-13D.
3.	Bronze body and stem.
4.	1/4 inch (6 mm) NPT inlet and outlet connections.
5.	1/4 inch (6 mm) test/drain port with a plug to facilitate draining of valve/gauge assemblies.
E.	Valve Repair Kits:
1.	Product: TESTanDRAIN Repair Kits. Available for all TESTanDRAIN Valve models: 1000, 1011, 2500, 2511, RemoteTEST Model 1200, and DRAINanTEST Model 1500.
F.	Locking Plate Kits:
1.	Product: TESTanDRAIN Locking Plate Kits. 
2.	Provides vandal resistance and prevents accidental alarm activation by locking the valve handle in the "OFF" position.
a.	Locking Plate: Carbon steel.
b.	Lock: 1-1/2 inches (38 mm) wide solid brass with a 1/4 inch (6.4 mm) chrome plated hardened steel shackle.
c.	For use with a 1 inch (25 mm), 1-1/4 inches (32 mm), 2 inches (51 mm) valves.
PART 3    EXECUTION
3.1	EXAMINATION
A.	Do not begin installation until substrates have been properly constructed and prepared.
B.	If substrate preparation is the responsibility of another installer, notify Architect in writing of unsatisfactory preparation before proceeding.
3.2	PREPARATION
A.	Clean surfaces thoroughly prior to installation.
B.	Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.
3.3	INSTALLATION
A.	Install in accordance with manufacturer's instructions, approved submittals and in proper relationship with adjacent construction.
B.	Test for proper operation and adjust until satisfactory results are obtained. 
3.4	FIELD QUALITY CONTROL
A.	Field Inspection: Coordinate field inspection in accordance with appropriate sections in Division 01.
B.	Manufacturer's Services: Coordinate manufacturer's services in accordance with appropriate sections in Division 01.
3.5	CLEANING AND PROTECTION
A.	Clean products in accordance with the manufacturer's recommendations. 
B.	Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION