SECTION 28 13 53.12

IP VIDEO INTERCOM SYSTEMS - IX AND IXG SERIES

Display hidden notes to specifier. (Don't know how? Click Here) 
 Copyright 2026 -  2026 ARCAT, Inc. - All rights reserved

PART 1    GENERAL
1.1	SECTION INCLUDES
A.	Audio/video entry security system:
1.	IP video intercom system. (Aiphone IX Series) (Aiphone IXG Series)
B.	Components for audio/video entry security systems:
1.	IP video tenant station. (IXG-2C7)
a.	Flush mount kit for tenant station. (IXG-FMK-2C7)
2.	IP video answering stations. (IX-MV7)
3.	IP video guard stations. (IXG-MK)
4.	Software answering station. (IX-SOFT)
5.	IP video entrance station. (IXG-DM7-HIDA)
a.	Flush mount box for entrance station. (IXG-DM7-BOX)
b.	Surface mount box for entrance station. (SBX-IXGDM7)
C.	IP Video Door Stations:
1.	Audio video stations. (IX-DV) (IX-DVF) (IX-DVF-L) (IX-DVF-PR) (IX-DVF-RA) (IX-DVF-2RA) (IX-DVF-4A) (IX-DVF-6) (IX-DVM) (IX-EA)
D.	Audio Only Door Stations:
1.	Audio stations. (IX-SSA) (IX-SSA-RA) (IX-SSA-2RA) (IX-SS-2G)
E.	IP Audio Substations:
1.	Audio substation. (IX-RS-B) (IX-RS-W)
F.	Lift control adaptor. (IXGW-LC)
G.	IP programmable relay adaptor. (IXW-MAA)
H.	Gateway adaptor for remote management, telephone dialing, and mobile application. (IXGW-TGW).
I.	Emergency and Assistance Towers:
1.	Lightweight emergency and assistance towers. (TW-SA) (TW-SE) (TW-TA) (TW-TE) (TW-TA-SP) (TW-TE-SP) (TW-TA-ARM) (TW-TE-ARM) (TW-TA-SP-ARM) (TW-TE-SP-ARM)
J.	Emergency and assistance wall boxes. (WB-CA) (WB-CE) (WB-HA) (WB-HE).
1.2	RELATED SECTIONS
A.	Section 28 18 00 - Security Access Detection Equipment.
B.	Section 28 13 53.10 - Security Video Intercom System.
1.3	REFERENCES
A.	American National Standards Institute (ANSI):
1.	ANSI/TIA/EIA 568 - Commercial Building Telecommunications Cabling Standard.
B.	International Organization for Standards (ISO):
1.	ISO 9001:2015 - Quality Management Systems - Requirements.
1.4	SUBMITTALS
A.	Submit under provisions of Section 01 30 00 - Administrative Requirements.
B.	Product Data: Manufacturer's data sheets on each product to be used, including:
1.	Preparation instructions and recommendations.
2.	Storage and handling requirements and recommendations.
3.	Installation methods.
C.	Shop Drawings: Submit the following:
1.	Wiring Diagrams: Indicate wiring for each item of equipment and interconnections between items of equipment.
2.	Include manufacturer's names, model numbers, ratings, power requirements, equipment layout, device arrangement, complete wiring point-to-point diagrams, and conduit layouts.
D.	Installation and Operation Manuals:
1.	Submit manufacturer's installation and operation manual, including operation instructions and component wiring diagrams.
2.	Provide detailed information required for Owner to properly operate equipment.
E.	Warranty: Submit manufacturer's standard warranty.
F.	Selection Samples: For each finish product specified, two complete sets of color chips representing manufacturer's full range of available colors and patterns.
G.	Verification Samples: For each finish product specified, two samples, minimum size 6 inches (150 mm) square, representing actual product, color, and patterns.
1.5	QUALITY ASSURANCE
A.	Manufacturer Qualifications: ISO 9001: 2015 certified company.
B.	Installer Qualifications: Factory trained and experienced with system installations of scope and size required for the Project.
C.	Mock-Up: Provide a mock-up for evaluation of surface preparation techniques and application workmanship.
1.	Finish areas designated by architect.
2.	Do not proceed with remaining work until workmanship, color, and sheen are approved by architect.
3.	Refinish mock-up area as required to produce acceptable work.
1.6	DELIVERY, STORAGE, AND HANDLING
A.	Delivery: Deliver materials to site in manufacturer's original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.
B.	Storage: Store materials in clean, dry indoor areas in accordance with manufacturer's instructions.
C.	Handling: Protect materials during handling and installation to prevent damage.
1.7	PROJECT CONDITIONS
A.	Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's absolute limits.
PART 2    PRODUCTS
2.1	MANUFACTURERS
A.	Acceptable Manufacturer: Aiphone Corp., which is located at:<BR />6670 185th Ave. NE<BR />Redmond, WA 98052 <BR />Toll Free Tel: 800-692-0200<BR />Tel: 425-455-0510<BR />Fax: 425-455-0071<BR />Email: request info (marketing@aiphone.com);Web: https://www.aiphone.com 
B.	Substitutions: Not permitted.
C.	Requests for substitutions will be considered in accordance with provisions of Section 01 60 00 - Product Requirements.
2.2	IP AUDIO/VIDEO ENTRY SECURITY SYSTEM
A.	Basis of Design:  Aiphone IX and IXG Series IP Video Intercom as manufactured by Aiphone Corporation. A complete network-based communication system for security applications in every market.
1.	ADA-compliant.
2.	IP camera integration.
3.	Systems with audio only components shall be configurable.
4.	Mobile app.
5.	All stations are PoE.
6.	Touchscreen entrance panel.
7.	Updates can be programmed remotely.
8.	Built-in reader options.
9.	Emergency tower and wall box mounting options available.
10.	Network Interface: 10 BASE-T/100 BASE-TX Ethernet (RJ-45).
11.	Network Protocols: IPv4, IPv6, TCP, UDP, SIP, HTTP, HTTPS, RTSP, RTP.
12.	Wire Type: Cat-5e or Cat-6.
2.3	COMPONENTS FOR IP AUDIO/VIDEO ENTRY SECURITY SYSTEM
A.	Product: IP Video Tenant Station, Model IXG-2C7 or IXG-2C7-L: Answer calls from an entrance station, guard station, or individual door station.
1.	Communication: Hands-free full duplex.
2.	Internal Call History: MicroSD card slot for added memory.
3.	Place calls to other stations and mobile apps within residential unit. 
4.	One-button concierge or guard call.
5.	Monitor door and entrance stations.
6.	T-Coil Hearing Aid Support; IXG-2C7-L only.
7.	Call elevator to floor with IXGW-LC.
8.	Screen: 7 inch (178 mm) LCD TFT touchscreen.
a.	Monitor resolution: 800 x 480.
9.	Consumption: Standby 1.9 W, Max 5.9 W.
10.	Operating Temperature: 32 to 104 degrees F (0 to 40 degrees C).
11.	Dimensions (HxWxD): 5-13/16 x 8-15/16 x 1 inch (148 x 227 x 25 mm).
12.	Flush Mount Kit for Tenant Station: IXG-FMK-2C7.
a.	Flush wall mounted.
b.	Panel Material: Self-extinguishing resin.
c.	Frame and Back Box Material: Self-extinguishing plastic.
d.	Dimensions:
1)	Panel and Frame (WxHxD): 11-7/16 x 7-13/16 x 1-3/16 inch (290 x 199 x 30 mm).
2)	Back Box (WxHxD): 10-7/16 x 6-5/8 x 1-9/16 inch (265 x 169 x 40 mm). 
B.	Product: IP Video Answering Station, Model IX-MV7: Answer calls from an entrance station, guard station, another answering station, individual door station, or SIP extension.
1.	Model IX-MV7-HB. Answering station. Black, handset.
2.	Model IX-MV7-HW-JP. Answering station. White, handset.
3.	Model IX-MV7-B. Answering station. Black, hands free.
4.	Model IX-MV7-W. Answering station. White, hands free.
5.	Create up to 8 speed dial buttons for calling, paging, or door release.
6.	Communication: Hands-free full duplex or handset on select models.
7.	Internal call history. MicroSD card slot for added memory.
8.	SIP Compatible.
9.	Place calls to other stations and mobile apps in the same or other units.
10.	Place live or pre-recorded pages to all or select groups of stations in the system.
11.	Monitor individual doors stations or monitor in sequence with scan monitor.
12.	Screen: 7 inch (178 mm) LCD TFT touchscreen.
13.	Monitor resolution: 800 x 480.
14.	Power Source: PoE (IEEE 802.3af Class 0).
15.	Consumption: 7.4W.
16.	Operating Temperature: 32 to 104 degrees F (0 to 40 degrees C).
17.	Dimensions without Handset (HxWxD): 6-3/4 x 8-11/16 x 1-1/4 inch (172 x 220 x 31.7 mm).
18.	Dimensions with Handset (HxWxD): 8-1/16 x 11 x 2-3/16 inch (204 x 280 x 55.5 mm).
19.	Mounting: Wall or desk mount with included frame and stand.
C.	Product: IP Video Guard Station, Model IXG-MK: Answer calls from an entrance station, guard station, another answering station, individual door station, or SIP extension.
1.	Place mass notifications to IXG-2C7/IXG-2C7-L tenant stations.
2.	Screen calls to tenant units from entrance stations with concierge mode.
3.	Create up to 8 speed dial buttons for calling, paging, or door release.
4.	Communication: Hands-free Full duplex or Handset.
5.	Internal call history. MicroSD card slot for added memory.
6.	SIP Compatible.
7.	Place calls to other stations and mobile apps in the same or other units. 
8.	Place live or pre-recorded pages to all or select groups of stations in the system.
9.	Monitor individual doors stations or monitor in sequence with scan monitor.
10.	Screen: 7 inch (178 mm) LCD TFT touchscreen.
11.	Monitor resolution: 800 x 480.
12.	Power Source: PoE (IEEE 802.3af Class 0).
13.	Consumption: 7.4W.
14.	Operating Temperature: 32 to 104 degrees F (0 to 40 degrees C).
15.	Dimensions: 8-1/16 x 11 x 2-3/16 inch (204 x 280 x 55.5 mm).
16.	Mounting: Wall or Desk Mount with included frame and stand.
D.	Product: Software Answering Station, Model IX-SOFT: Answer calls from an entry station, guard station, another answering station, individual door station, or SIP extension.
1.	Communication: Utilizes PC speaker and microphone.
2.	Place calls to other stations and mobile apps in the same or other units. 
3.	Place live or pre-recorded pages to all or select groups of stations in the system.
4.	Monitor individual doors stations or monitor in sequence with scan monitor.
5.	Create up to 50 speed dial buttons for calling, paging, or door release.
6.	Create a map showing the locations of different intercoms on the site.
7.	Supports Windows 7 Professional, Windows 7 Enterprise, Windows 7 Ultimate Windows 8.1, Windows 8.1 Pro, Windows 8.1 Enterprise Windows 10 Home, Windows 10 Pro, Windows 10 Enterprise, Windows 10 Education Windows 11 Home, Windows 11 Pro, Windows 11 Enterprise.
8.	32 or 64 bit versions available.
E.	Product: IP Video Entrance Station, Model IXG-DM7-HIDA: Place video calls to all answering stations, tenant stations, apps, SIP extensions (requires compatible IP-PBX), and PC answering stations, in a unit.
1.	Answering stations or software can engage the door release output on the entrance station.
2.	Stream video feed to compatible NVR/VMS.
3.	Screen: 7 inch (178 mm) TFT LCD display directory screen for calling a tenant or entering an access entry code.
a.	Monitor resolution: 800 x 480.
b.	Communication: Full duplex.
4.	On-board recording with microSD card.
5.	Hands-free audio communication.
6.	HD camera.
7.	Up to 9,999 names/numbers can be stored.
8.	Programmable Contact Inputs: 4.
9.	Programmable Relay Outputs: 2.
10.	SIP Compatible.
11.	Program access codes for tenant access.
12.	Motion sensor to activate LCD.
13.	Built-in HID reader for card access.
14.	Material: 
a.	Panel: Stainless steel.
b.	Main unit - Case: Flame retardant ABS resin.
c.	LCD Display: Glass.
d.	Chassis: Die-cast aluminum.
e.	Weather resistant: IP65.
f.	Impact resistance: IK08 (touchscreen: IK10).
15.	Tamper and impact sensors.
16.	Power Source: PoE (IEEE 802.3af Class 0).
17.	Operating Temperature: -22 to 140 degrees F (-30 to 60 degrees C).
18.	Dimensions (HxWxD): 13-11/16 x 7-3/16 inch (347 x 182 mm).
19.	Flush Mount with IXG-DM7-BOX:
a.	Steel construction.
b.	Conduit Knockouts: Back of Box: 2. Top of Box: 2. Bottom of Box: 2.
c.	Dimensions (HxWxD): 12-1/2 x 6-1/8 x 2-3/8 inch (317 x 156 x 60 mm).
d.	Must be used to flush mount the IXG-DM7-HIDA. Sold separately for pre-installation convenience.
20.	Surface mount with SBX-IXGDM7. See the "Mounting Enclosure" Paragraph in this article.
F.	IP Video Door Stations:
1.	Product: Model IX-DV. Video Door Station. Surface Mount. Hands Free. Place calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
a.	Calls include video and two-way audio.
b.	Answering stations can engage the door release output on the door station. 
c.	The video feed can be streamed via ONVIF Profile S.
d.	Material: Aluminum Diecast.
1)	Weather resistant: IP54.
2)	Impact resistant: IK08.
e.	SIP Compatible.
f.	Programmable Relay Outputs: 2.
g.	Programmable Option Inputs: 6.
h.	Consumption: 5.28 W.
i.	Power Source: PoE (IEEE 802.3af Class 0).
j.	PoE passthrough (requires PoE+).
k.	600 ohm audio output.
l.	Operating Temperature: -40 to 140 degrees F (-40 to 60 degrees C).
m.	Dimensions (HxWxD): 8-1/16 x 4-1/2 x 2-1/16 inch (207 x 115 x 52.5 mm).
2.	Product: Model IX-DVF. Video Door Station. Flush Mount. Hands Free. Place calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
a.	Calls include video and two-way audio.
b.	Answering stations can engage the door release output on the door station. 
c.	The video feed can be streamed via ONVIF Profile S.
d.	Material: Stainless Steel.
1)	Weather resistant: IP65.
2)	Impact resistant: IK08.
e.	SIP Compatible.
f.	Programmable Relay Outputs: 2.
g.	Programmable Option Inputs: 6.
h.	Consumption: 5.28 W.
i.	Power Source: PoE (IEEE 802.3af Class 0).
j.	PoE passthrough (requires PoE+).
k.	600 ohm audio output.
l.	Operating Temperature: -40 to 140 degrees F (-40 to 60 degrees C).
m.	Dimensions (HxW): 10-7/16 x 5-7/8 inch (265 x 150 mm).
n.	Surface mount with SBX-IDVF. See the "Mounting Enclosure" Paragraph in this article.
3.	Product: Model IX-DVF-L. Video Door Station. Flush Mount. Hands Free. T-Coil Support. Place calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
a.	Calls include video and two-way audio.
b.	Answering stations can engage the door release output on the door station. 
c.	The video feed can be streamed via ONVIF Profile S.
d.	Material: Stainless Steel.
1)	Weather resistant: IP65.
2)	Impact resistant: IK08.
e.	SIP Compatible.
f.	T-Coil Hearing Aid Support.
g.	Programmable Relay Outputs: 2.
h.	Programmable Option Inputs: 6.
i.	Consumption: 5.28 W.
j.	Power Source: PoE (IEEE 802.3af Class 0).
k.	PoE passthrough (requires PoE+).
l.	600 ohm audio output.
m.	Operating Temperature: -40 to 140 degrees F (-40 to 60 degrees C).
n.	Dimensions (HxW): 11-11/16 x 7 inch (297 x 178 mm).
o.	Surface mount with SBX-IDVFRA. See the "Mounting Enclosure" Paragraph in this article.
4.	Product: Model IX-DVF-PR. Video Door Station. Flush Mount. Hands Free. AC-PROX-1G proximity reader
a.	Place calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
b.	Calls include video and two-way audio.
c.	Answering stations can engage the door release output on the door station. 
d.	The video feed can be streamed via ONVIF Profile S.
e.	Material: Stainless Steel.
1)	Weather resistant: IP65.
2)	Impact resistant: IK08.
f.	SIP Compatible.
g.	Built-in AC-PROX-1G proximity reader.
h.	Programmable Relay Outputs: 2.
i.	Programmable Option Inputs: 6.
j.	Consumption: 5.28 W.
k.	Power Source: PoE (IEEE 802.3af Class 0).
l.	PoE passthrough (requires PoE+).
m.	600 ohm audio output.
n.	Operating Temperature:
1)	Door Station: -40 to 140 degrees F (-40 to 60 degrees C).
2)	Card Reader: Operating Temperature: -31 to 140 degrees F (-35 to 60 degrees).
o.	Dimensions (HxW): 11-11/16 x 7 inch (297 x 178 mm).
p.	Surface mount with SBX-IDVFRA. See the "Mounting Enclosure" Paragraph in this article.
5.	Product: Model IX-DVF-RA. Video Door Station. Flush Mount. Emergency Button. Place calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
a.	Calls include video and two-way audio.
b.	Answering stations can engage the door release output on the door station. 
c.	The video feed can be streamed via ONVIF Profile S.
d.	Material: Stainless Steel.
1)	Weather resistant: IP65.
2)	Impact resistant: IK08.
e.	SIP Compatible.
f.	Red Emergency Mushroom Button.
g.	Emergency Signage in English and Braille.
h.	Programmable Relay Outputs: 2.
i.	Programmable Option Inputs: 5.
j.	Consumption: 5.28 W.
k.	Power Source: PoE (IEEE 802.3af Class 0).
l.	PoE passthrough (requires PoE+).
m.	600 ohm audio output.
n.	Operating Temperature: -40 to 140 degrees F (-40 to 60 degrees C).
o.	Dimensions (HxW): 11-11/16 x 7 inch (297 x 178 mm).
p.	Surface mount with SBX-IDVFRA. See the "Mounting Enclosure" Paragraph in this article.
6.	Product: Model IX-DVF-2RA. Video Door Station. Flush Mount. Emergency and Call Buttons. Place calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
a.	Calls include video and two-way audio.
b.	Answering stations can engage the door release output on the door station. 
c.	The video feed can be streamed via ONVIF Profile S.
d.	Material: Stainless Steel.
1)	Weather resistant: IP65.
2)	Impact resistant: IK08.
e.	SIP Compatible.
f.	Red Emergency Mushroom Button and Call Button.
g.	Emergency Signage in English and Braille.
h.	Programmable Relay Outputs: 2.
i.	Programmable Call and Emergency Call buttons: 2.
j.	Programmable Option Inputs: 5.
k.	Consumption: 5.28 W.
l.	Power Source: PoE (IEEE 802.3af Class 0).
m.	PoE passthrough (requires PoE+).
n.	600 ohm audio output.
o.	Operating Temperature: -40 to 140 degrees F (-40 to 60 degrees C).
p.	Dimensions (HxW): 11-11/16 x 7 inch (297 x 178 mm).
q.	Surface mount with SBX-IDVFRA. See the "Mounting Enclosure" Paragraph in this article.
7.	Product: Model IX-DVF-4A. Video Door Station. Flush Mount. 4 Individual Call Buttons. Place calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
a.	Place calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
b.	Calls include video and two-way audio.
c.	Answering stations can engage the door release output on the door station. 
d.	The video feed can be streamed via ONVIF Profile S.
e.	Material: Stainless Steel.
1)	Weather resistant: IP65.
2)	Impact resistant: IK08.
f.	SIP Compatible.
g.	Programmable Relay Outputs: 2.
h.	Programmable Call Buttons: 4.
i.	Programmable Option Inputs: 2.
j.	Consumption: 5.28 W.
k.	Power Source: PoE (IEEE 802.3af Class 0).
l.	PoE passthrough (requires PoE+).
m.	600 ohm audio output.
n.	Operating Temperature: -40 to 140 degrees F (-40 to 60 degrees C).
o.	Dimensions (HxW): 13-11/16 x 7-3/16 inch (348 x 183 mm).
p.	Surface mount with SBX-IXGDM7. See the "Mounting Enclosure" Paragraph in this article.
8.	Product: Model IX-DVF-6. Video Door Station. Flush Mount. 6 Individual Call Buttons. Place calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
a.	Calls include video and two-way audio.
b.	Answering stations can engage the door release output on the door station. 
c.	The video feed can be streamed via ONVIF Profile S.
d.	Material: Stainless Steel.
1)	Weather resistant: IP65.
2)	Impact resistant: IK08.
e.	SIP Compatible.
f.	Programmable Relay Outputs: 2.
g.	Programmable Call Buttons: 6.
h.	Consumption: 5.28 W.
i.	Power Source: PoE (IEEE 802.3af Class 0).
j.	PoE passthrough (requires PoE+).
k.	600 ohm audio output.
l.	Operating Temperature: -40 to 140 degrees F (-40 to 60 degrees C).
m.	Dimensions (HxW): 13-11/16 x 7-3/16 inch (348 x 183 mm).
n.	Surface mount with SBX-IXGDM7. See the "Mounting Enclosure" Paragraph in this article.
9.	Product: Model IX-DVM. Video Door Station. Surface Mount. Mullion Mount. Touchless Call Sensor. Place calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
a.	Calls include video and two-way audio.
b.	Answering stations can engage the door release output on the door station. 
c.	The video feed can be streamed via ONVIF Profile S.
d.	Material: Aluminum Diecast.
1)	Weather resistant: IP65.
2)	Impact resistant: IK08.
e.	SIP Compatible.
f.	Touchless Call Sensor.
g.	Mullion Mountable.
h.	Programmable Relay Outputs: 1.
i.	Programmable Option Inputs: 1.
j.	Power Source: PoE (IEEE 802.3af Class 0).
k.	Consumption: 4.6 W.
l.	Operating Temperature: -40 to 140 degrees F (-40 to 60 degrees C).
m.	Dimensions (HxWxD): 6-7/8 x 1-7/8 x 1-5/16 inch (175 x 48 x 34 mm).
10.	Product: Model IX-EA. Video Door Station. Surface Mount. Place calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
a.	Calls include video and two-way audio.
b.	Answering stations can engage the door release output on the door station. 
c.	The video feed can be streamed via ONVIF Profile S.
d.	Material: Fire retardant ABS resin.
1)	Weather resistant: IP54.
e.	SIP compatible.
f.	Programmable Relay Outputs: 1.
g.	Programmable Option Inputs: 1.
h.	Power Source: PoE (IEEE 802.3af Class 0).
i.	Consumption: 5.18 W.
j.	600 ohm audio output.
k.	Operating Temperature: -40 to 140 degrees F (-40 to 60 degrees C).
l.	Dimensions (HxWxD): 6-5/16 x 3-15/16 x 1-3/4 inch (160 x 100 x 43.5 mm).
G.	Audio Only Door Stations:
1.	Product: Model IX-SSA. Audio Door Station. Flush Mount. Places calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
a.	Calls include two-way audio.
b.	Answering stations can engage the door release output on the door station.
c.	Material: Stainless Steel.
1)	Weather resistant: IP65.
2)	Impact resistant: IK08.
d.	SIP Compatible.
e.	Programmable Relay Outputs: 2.
f.	Programmable Option Inputs: 6.
g.	Consumption: 3.36 W.
h.	Power Source: PoE (IEEE 802.3af Class 0).
i.	PoE passthrough (requires PoE+).
j.	Operating Temperature: -40 to 140 degrees F (-40 to 60 degrees C).
k.	Dimensions (HxW): 10-7/16 x 5-7/8 inch (265 x 150 mm).
l.	Surface mount with SBX-IDVF. See the "Mounting Enclosure" Paragraph in this article.
2.	Product: Model IX-SSA-RA. Audio Door Station. Flush Mount. Emergency Button.
a.	Places calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
b.	Calls include two-way audio.
c.	Answering stations can engage the door release output on the door station. 
d.	Material: Stainless Steel.
1)	Weather resistant: IP65.
2)	Impact resistant: IK08.
e.	SIP Compatible.
f.	Red Emergency Mushroom Button.
g.	Emergency Signage in English and Braille.
h.	Programmable Relay Outputs: 2.
i.	Programmable Option Inputs: 5.
j.	Consumption: 3.36 W.
k.	Power Source: PoE (IEEE 802.3af Class 0).
l.	PoE passthrough (requires PoE+).
m.	Operating Temperature: -40 to 140 degrees F (-40 to 60 degrees C).
n.	Dimensions (HxW): 11-11/16 x 7 inch (297 x 178 mm).
o.	Surface mount with SBX-IDVFRA. See the "Mounting Enclosure" Paragraph in this article.
3.	Product: Model IX-SSA-2RA. Audio Door Station. Flush Mount. Emergency and Call Buttons. Places calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
a.	Calls include two-way audio.
b.	Answering stations can engage the door release output on the door station. 
c.	Material: Stainless Steel.
1)	Weather resistant: IP65.
2)	Impact resistant: IK08.
d.	SIP Compatible.
e.	Red Emergency Mushroom Button and Call Button.
f.	Emergency Signage in English and Braille.
g.	Programmable Relay Outputs: 2.
h.	Programmable Option Inputs: 5.
i.	Consumption: 3.36 W.
j.	Power Source: PoE (IEEE 802.3af Class 0).
k.	PoE passthrough (requires PoE+).
l.	Operating Temperature: -40 to 140 degrees F (-40 to 60 degrees C).
m.	Dimensions (HxW): 11-11/16 x 7 inch (297 x 178 mm).
n.	Surface mount with SBX-IDVFRA. See the "Mounting Enclosure" Paragraph in this article.
4.	Product: Model IX-SS-2G. Audio Door Station. Flush Mount. Hands Free. Places calls to answering stations, VoIP Phones (requires compatible IP-PBX), mobile apps, or IX-SOFT PC answering stations. 
a.	Calls include two-way audio.
b.	Answering stations can engage the door release output on the door station. 
c.	Material: Stainless Steel.
1)	Weather resistant: IP65.
2)	Impact resistant: IK08.
d.	SIP Compatible.
e.	Programmable Relay Outputs: 1.
f.	Programmable Option Inputs: 1.
g.	Power Source: PoE (IEEE 802.3af Class 0).
h.	Consumption: 3.36 W.
i.	Operating Temperature: -40 to 140 degrees F (-40 to 60 degrees C).
j.	Dimensions (HxW): 4-3/4 x 4-3/4 inch (120 x 120 mm).
k.	Surface mount with SBX-2G/A. See the "Mounting Enclosure" Paragraph in this article.
H.	IP Audio Substation: IX-RS:
1.	Product: Model IX-RS-B. Substation. Black, handset.
2.	Product: Model IX-RS-W. Substation. White, handset.
3.	Answer calls from an entry station, guard station, another answering station, individual door station, or SIP extension. 
4.	Place calls to a preconfigured destination.
5.	Release door or entrance station with capacitive button. 
6.	Receive pages from answering stations. 
7.	Communication: Hands-free Full duplex or Handset.
8.	SIP Compatible.
a.	Programmable Relay Outputs: 1.
b.	Programmable Option Inputs: 1.
9.	2-watt, 8 ohm speaker output.
10.	Power Source: PoE (IEEE 802.3af Class 0).
11.	Consumption: 4.32W.
12.	Operating Temp: 32 to 104 degrees F (0 to 40 degrees C).
13.	Dimensions (HxWxD): 7-9/16 x 3-9/16 x 2-5/8 inch (192 x 90 x 67 mm).
I.	Product: Lift control adapter. Model IXGW-LC. Connects to site's elevator controls via programmable outputs.
1.	Grant access to preconfigured floors via integration with site's elevator controls. Assign each output to one or multiple units.
2.	Summon elevator to preconfigured floors from tenant stations using Elevator Call Button.
3.	20 Form C relays and up to 16 adaptors per building.
a.	Relay Rating: 24 V AC/DC 500 mA.
4.	Power Source: PoE (IEEE 802.3af Class 0).
5.	Consumption: Standby 2.1 W, Max 4.4 W.
6.	LAN: Ethernet (10 BASE-T, 100 BASE-TX).
7.	Operating Temp: 14 to 122 degrees F (-10 to 50 degrees C).
8.	Dimensions (HxWxD): 4-1/4 x 8-1/4 x 2-3/8 inch (108 x 210 x 60 mm).
J.	Product: IP Programmable relay adaptor. Model IXW-MAA. Provides configurable relay outputs that can mirror the outputs on other stations.
1.	10 Form C relays and up to 500 adaptors per configuration.
a.	Relay Rating: 24 V AC/DC 500 mA.
2.	Power Source: PoE (IEEE 802.3af Class 0).
3.	Consumption: Standby 2.1 W, Max 4.48 W.
4.	LAN: Ethernet (10 BASE-T, 100 BASE-TX).
5.	Operating Temp: 14 to 122 degrees F (-10 to 50 degrees C).
6.	Dimensions (HxWxD): 4-1/4 x 8-1/4 x 2-3/8 inch (108 x 210 x 60 mm).
K.	Product: Gateway adapter. Model: IXGW-TGW. Enables mobile apps on the system. App is available for iOS and Android and grants similar features to answering stations.
1.	Enables a cellular connection as the primary or secondary network connection.
2.	Enables telephone calling via included SIM card.
3.	Grants access to Remote Management options in AiphoneCloud.
4.	Power Source: PoE.
5.	DIN rail mountable.
6.	Simultaneous Call Paths: 8.
7.	Supports up to 9,999 IXG apps.
8.	Wireless Connection: 4G LTE.
9.	Consumption: Standby 2.1 W, Max 2.9 W.
10.	LAN: Ethernet (10 BASE-T, 100 BASE-TX).
11.	Packet Delivery: Unicast, Multicast.
12.	Protocol: IPv4/v6, TCP, UDP, SIP, HTTPS, RTP, RTCP, SRTP, SRTCP, IGMP, MLD, SFTP, DHCP, NTP, DNS, MQTT, ICE, DTLS, SDP.
13.	Channel: 8.
14.	Encryption: TLS 1.2.
15.	Operating Temperature: 14 to 122 degrees F (-10 to 50 degrees C).
16.	Dimensions (HxWxD): 4-1/4 x 8-1/4 x 2-3/8 inch (108 x 210 x 60 mm).
L.	Emergency and Assistance Towers:
1.	Lightweight tower design available in the following configurations:
a.	Product: Mid-level Tower Models. TW-SA.
b.	Product: Mid-level Tower Models. TW-SE.
c.	Product: High-level Tower Models. TW-TA.
d.	Product: High-level Tower Models. TW-TE.
e.	Product: High-level Tower with Speaker Models. TW-TA-SP.
f.	Product: High-level Tower with Speaker Models. TW-TE SP.
g.	Product: High-level Tower with Camera Arm Models. TW-TA-ARM.
h.	Product: High-level Tower with Camera Arm Models. TW-TE-ARM.
i.	Product: High-level Tower with Camera Arm and Speaker Models. TW-TA-SP-ARM.
j.	Product: High-level Tower with Camera Arm and Speaker Models. TW-TE-SP-ARM.
2.	Top Cover: Light cage with blue beacon and strobe.
3.	UL Listed electrical box included in base.
4.	Material: Aluminum 6061-T6.
5.	Color: Blue.
6.	Lettering Color: White. 
7.	Access panel on back of the tower for easier installation and wiring.
a.	One Panel at Base: Model TW-S. Mid-level.
b.	One Panel at Base and One Panel at the Middle. Model TW-T. High-level. 
8.	Mounting studs at middle and base for internal product (power supply, relay, etc.).
9.	Weather and vandal resistant.
10.	Mounting: TW-MKL L-brackets and anchor bolts to foundation meeting size requirements of manufacturer.
11.	Options: 
a.	Assistance and emergency signage.
b.	Camera arm module with universal pipe threading (1.50 inch NPT threading x 1 inch (25 mm) long).
c.	Speaker with internal amplifier and volume control board.
12.	Dimensions (HxWxD):
a.	Mid-Level Tower: 73 x 8 x 8 inch (1854 x 203 x 203 mm). Weight: 43 lbs.
b.	High-Level Tower: 112 x 8 x 8 inch (2845 x 203 x 203 mm). Weight: 68 lbs.
c.	High-Level Tower with Speaker: 127 x 8 x 8 inch (3226 x 203 x 203 mm). Weight: 87 lbs.
d.	High-Level Tower with Camera Arm: 174 x 8 x 15-3/4 inch (4420 x 203 x 400 mm). Weight: 99 lbs.
M.	Emergency and Assistance Wall Boxes:
1.	Slim profile stainless steel wall box with beacon available in four configurations.
a.	Box with light cage and assistance lettering. WB-CA.
b.	Box with light cage and emergency lettering. WB-CE.
c.	Box with hooded light and assistance lettering. WB-HA.
d.	Box with hooded light and emergency lettering. WB-HE.
2.	Lettering Color:
a.	Assistance Lettering: Blue.
b.	Emergency Lettering: Red.
3.	Beacon / Strobe is always lit; flashes during emergency call-in (requires 24V DC).
4.	LED light for station illumination in middle module (requires 24V DC).
5.	UL Listed electrical box included inside.
6.	Call button mounting height and signage meets ADA regulations.
7.	Compatibility: Use with IX-DVF-2RA, IX-DVF-RA, IX-SSA-2RA, and IX-SSA-RA.
8.	Compatibility with Non-Emergency Call Stations when using the TW-SPL: IX-DVF, 
9.	IX-SSA.
N.	Mounting Enclosures:
1.	Stainless Steel Enclosure Model SBX-IDVF:
a.	18-Gauge Stainless Steel Surface Mount Box for IX-DVF and IX-SSA, designed for surface mounting door station.
b.	Conduit Knockouts: 1 on bottom of box.
c.	Dimensions (HxW): 10-7/16 x 5-15/16 inch (265 x 151 mm).
1)	Top depth: 3-5/16 inch (84 mm).
2)	Bottom depth: 2-5/16 inch (59 mm).
d.	Weather and vandal resistant.
e.	Inside space for cabling.
f.	Mounting: 1 or 2-gang mounting hole pattern on back of box.
g.	Built-in rain hood.
h.	Opening at bottom for drainage.
2.	Stainless Steel Enclosure Model SBX-IDVFRA:
a.	18-Gauge Stainless Steel Surface Mount Box for IX-DVF-RA, IX-DVF-2RA, IX-SSA-RA, IX-SSA-2RA, IX-DVF-PR.
b.	Dimensions (HxW): 11-11/16 x 7 inch (297 x 178 mm).
1)	Top depth: 3-5/16 inch (84 mm).
2)	Bottom depth: 2-5/16 inch (59 mm).
c.	Weather resistant.
d.	Vandal resistant.
e.	Inside space for cabling.
f.	Mounting: 1 or 2-gang mounting hole pattern on back of box.
g.	Built-in rain hood.
h.	Opening at bottom for drainage.
3.	Stainless Steel Enclosure Model SBX-IXGDM7:
a.	18-Gauge Stainless Steel Surface Mount Box for IXG-DM7-HIDA, IX-DVF-4A, and IX-DVF-6.
b.	Conduit Knockouts: 1 on bottom of box.
c.	Dimensions (HxW): 13-3/4 x 7-5/16 inch (349 x 186 mm).
1)	Top depth: 3-5/16 inch (84 mm).
2)	Bottom depth: 2-5/16 inch (59 mm).
d.	Weather resistant.
e.	Vandal resistant.
f.	Inside space for cabling.
g.	Mounting: 1 or 2 gang mounting hole pattern on back of box.
h.	Built-in rain hood.
i.	Opening at bottom for drainage.
4.	Stainless Steel Enclosure Model SBX-2G/A:
a.	18-Gauge Stainless Steel Surface Mount Box for IX-SS-2G.
b.	Conduit Knockouts: 1 on bottom of box.
c.	Dimensions (HxW): 4-13/16 x 4-7/8 inch (122 x 124 mm).
1)	Top depth: 4 inch (102 mm).
2)	Bottom depth: 3-9/16 inch (91 mm).
d.	Weather and vandal resistant.
e.	Inside space for cabling.
f.	Mounting: 1 gang mounting hole pattern on back of box.
g.	Built-in rain hood.
h.	Opening at bottom for drainage.
PART 3    EXECUTION
3.1	EXAMINATION
A.	Examine areas to receive integrated security and communication system.
B.	Notify architect of conditions that would adversely affect installation or subsequent use.
C.	Do not begin installation until unacceptable conditions are corrected.
3.2	PREPARATION
A.	Verify the following compliance before starting installation.
1.	All units, except for the entrance station and door stations, are designed for indoor use only. Do not use outdoors.
2.	The unit turns inoperative during power failure.
3.	In areas where broadcasting station antennas are close by, intercom system may be affected by radio frequency interference.
4.	Keep the intercom wires at least 1 foot (30 cm) away from strong electrical wiring (AC 100-240 V) including wiring for inverter electrical appliances. Noise and malfunction could result.
5.	Keep the unit more than 3.3 feet (1 m) away from radio or TV set.
6.	If a strong light shines on the main unit screen, the picture will turn white or only silhouettes will be visible.
7.	Other manufacturers' devices (such as sensor, detectors, door releases) used with this system, comply with the manufacturer's installation requirements.
8.	The LCD panel is manufactured with very high precision techniques, but it inevitably will have a very small portion of its picture elements always lit or not lit at all. This is not considered a unit malfunction. Please be aware of this in advance.
9.	The sensor of an entrance station (Integrated type) may activate due to moving shadows or moving tree branches, etc. and cause a message to display.
3.3	INSTALLATION
A.	Install integrated security and communication system in accordance with manufacturer's instructions at locations indicated on the drawings.
B.	Mount equipment plumb, level, square, and secure. For video entrance stations and video door stations, comply with manufacturer's design requirements to provide optimum picture quality of station monitoring.
3.4	SET-UP AND ADJUSTING
A.	Adjust integrated security and communication system for proper operation in accordance with manufacturer's instructions.
3.5	DEMONSTRATION AND TRAINING
A.	Demonstration:
1.	Demonstrate that integrated security and communication system function properly.
2.	Perform demonstration at final system inspection by qualified representative of manufacturer.
B.	Instruction and Training:
1.	Provide instruction and training of owner's personnel as required for operation of integrated security and communication system.
2.	Provide hands-on demonstration of operation of system components and complete system, including user-level program changes and functions.
3.	Provide instruction and training by qualified representative of manufacturer.
3.6	PROTECTION
A.	Protect installed integrated security and communication system from damage during construction.

END OF SECTION