SECTION 28 42 00

GAS DETECTION

Display hidden notes to specifier. (Don't know how? Click Here)

Copyright 2025 - 2025 ARCAT, Inc. - All rights reserved

** NOTE TO SPECIFIER ** American Gas Safety; control and detection panels.
This section is based on the products of American Gas Safety, which is located at:
6304 Benjamin Rd., Suite 512
Tampa, FL 33634
Tel: 727-608-4375
Fax: 727-530-0428
Email: request info (info@americangassafety.com)
Web: https://americangassafety.com  
 [ Click Here ] for additional information.
American Gas Safety (AGS) is the number one manufacturer of gas safety & control solutions in North America, delivering high-quality, internationally recognized products. Our comprehensive range includes fixed gas detection systems, gas safety controllers, gas shut-off controls, and water leak detection systems, all designed and manufactured to meet rigorous UL and CE standards.

- GENERAL

  - SECTION INCLUDES

** NOTE TO SPECIFIER ** Delete items below not required for project.

    - Gas Monitors.

    - Detectors.

    - TFT Detectors.

    - Isolation Controllers.

    - Ventilation Controllers.

    - Accessories.

  - REFERENCES

** NOTE TO SPECIFIER ** Delete references from the list below that are not actually required by the text of the edited section.

    - European Standards:

      - EMC Directive 2014/30/EU.

      - EN 50270, Electromagnetic Compatibility; 2015.

    - Federal Communications Commission (FCC):

      - FCC Part 15 Regulation; current edition.

    - Underwriters Laboratories (UL):

      - UL 2075, Gas and Vapor Detectors and Sensors; 2025.

      - UL 61010-1, Standard for Safety Requirements for Electrical Equipment for Measurement, Control, and Laboratory Use; Part 1: General Requirements, 3rd Edition; 2024.

  - SUBMITTALS

    - Submit under provisions of Section 01 30 00.

    - Product Data:

      - Manufacturer's data sheets on each product to be used.

      - Preparation instructions and recommendations.

      - Storage and handling requirements and recommendations.

      - Typical installation methods.

** NOTE TO SPECIFIER ** Delete if not applicable to product type.

    - Verification Samples: Two representative units of each type, size, pattern, and color.

    - Shop Drawings: Include details of materials, construction, and finish. Include relationship with adjacent construction.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: Company specializing in manufacturing products specified in this section with a minimum of five years documented experience.

    - Installer Qualifications: Company specializing in performing Work of this section with minimum two years documented experience with projects of similar scope and complexity.

    - Source Limitations: Provide each type of product from a single manufacturing source to ensure uniformity.

  - PRE-INSTALLATION CONFERENCE

    - Convene a conference approximately two weeks before scheduled commencement of the Work.

    - Attendees to include Architect, Contractor and trades involved.

    - Agenda to include schedule, responsibilities, critical path items and approvals.

  - DELIVERY, STORAGE, AND HANDLING

    - Store and handle in strict compliance with manufacturer's written instructions and recommendations.

    - Protect from damage due to weather, excessive temperature, and construction operations.

  - PROJECT CONDITIONS

    - Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's recommended limits.

  - WARRANTY

    - Manufacturer's standard limited warranty unless indicated otherwise.

- PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer: American Gas Safety, which is located at:
6304 Benjamin Rd., Suite 512
Tampa, FL 33634
Tel: 727-608-4375
Fax: 727-530-0428
Email: request info (info@americangassafety.com);Web: https://americangassafety.com

** NOTE TO SPECIFIER ** Delete one of the following two paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

    - Substitutions: Not permitted.

    - Requests for substitutions will be considered in accordance with the provisions of Section 01 60 00.

** NOTE TO SPECIFIER ** Delete article if not required.

  - GAS MONITORS

    - Basis of Design: Merlin GM 100 Dual Gas Monitor, as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Material: ABS Polycarbonate Flame Retardant, Rated IP65 with Splash Guard.

      - Size: 5.95 x 4.37 x 1.97 inch (151 x 111 x 50 mm).

      - Electrical:

        - Power Low Voltage: Nominal 24V AC/DC.

        - Wiring: 127 Units.

      - IO:

        - Digital Output:

          - BACnet MS/TP.

          - Modbus RTU, RS485.

        - SPST Signal Relay Output: 70mA 30V.

      - Operating Temperature: Minus 4 to 122 Degrees F (Minus 20 to 50 Degrees C).

      - Storage Temperature: 32 to 86 Degrees F (0 to 30 Degrees C).

      - Humidity:

        - 15 to 90 percent RH, continuous.

        - 0 to 99 percent, intermittent.

        - Non-condensing.

      - Audible Alarm: Internal greater than 85 dB.

    - Basis of Design: GM200 Single or Dual Channel Gas + PM10 Monitor, as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Material: ABS Flame Retardant UL94 V0.

      - Size: 8.2 x 5.7 x 2.1 inch (210 x 145 x 55 mm).

      - Electrical:

        - Power Input:

          - 90-250VAC.

          - 24V AC/DC (12-32V).

          - 50/60 HZ.

        - Wiring: RS485, 127 Units.

      - IO:

        - Digital Output 1: Modbus RTU and BACnet MS/TP, field selectable.

        - Signal 1: Dry Contact 1A, 60 VDC.

        - Latching Relay 1: Dry Contact 10A at 230V.

        - Latching Relay 2: Dry Contact 10A at 230V.

        - Analogue:

          - 0-10V.

          - 4-20mA.

      - Operating and Storage Temperature: Minus 4 to 122 Degrees F (Minus 20 to 50 Degrees C).

      - Humidity:

        - 15 to 90 percent RH, continuous.

        - 0 to 99 percent, intermittent.

        - Non-condensing.

      - Audible Alarm: Internal greater than 80 dB.

** NOTE TO SPECIFIER ** Delete article if not required.

  - DETECTORS

    - Basis of Design: AGSHiS, Hydrogen Gas Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: Detector i-S

      - Target Gas: H, Hydrogen.

      - Maximum Power Consumption: 1.8W.

      - Power Rating: 12-24V AC or DC.

      - Size: 5.95 x 4.37 x 1.97 inch (151 x 111 x 50 mm).

      - Housing Material: ABS PA765, Flame Retardant, UL 94V-1.

      - Wiring:

        - Minimum 2.5mm2.

        - 75 Degrees C.

        - Tinned Copper.

      - Mounting:

        - Safe Zone.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C).

      - Storage Temperature: 32 to 122 Degrees F (0 to 50 Degrees C).

      - Audible Alarm: Internal greater than 65 dB at 3.28-feet (1 m), quiet conditions.

    - Basis of Design: AGSCO2iS, CO2 Storage Tank Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: AGSCO2iS-50K Detector.

      - Target Gas: CO2, Carbon Dioxide.

      - Power Consumption: 90mA maximum at 24VDC.

      - DC Power: 12-32 VDC, Nominal 24 VDC.

      - Size: 5.95 x 4.37 x 1.97 inch (151 x 111 x 50 mm).

      - Housing Material: ABS Polylac, PA765.

      - Wiring:

        - #18-24AWG Power Pair.

        - #18-AWG Data Pair.

        - Tinned Copper.

      - Mounting:

        - 1-foot above finished floor.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), non-condensing.

      - Storage Temperature: Minus 13 to 122 Degrees F (Minus 25 to 50 Degrees C).

      - Audible Alarm: Internal greater than 95dB at 3.28-feet (1 m), quiet conditions.

    - Basis of Design: AGSCOiS, Carbon Monoxide Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: Detector i-S.

      - Target Gas: CO, Carbon Monoxide.

      - Power Consumption: Maximum 1.8W.

      - Power Rating: 12-24V AC or DC.

      - Size: 5.95 x 4.37 x 1.97 inch (151 x 111 x 50 mm).

      - Housing Material: ABS PA765, Flame Retardant, UL 94V-1.

      - Wiring:

        - Minimum 2.5mm2.

        - 75 Degrees C.

        - Tinned Copper.

      - Mounting:

        - Safe Zone.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C).

      - Storage: 32 to 122 Degrees F (0 to 50 Degrees C).

      - Audible Alarm: Internal greater than 95dB at 3.28-feet (1 m), quiet conditions.

    - Basis of Design: AGSNGiS, Natural Gas Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: Detector i-S.

      - Target Gas: NG, Natural Gas.

      - Power Consumption: Maximum 1.8W.

      - Power Rating: 12-24V AC or DC.

      - Size: 5.95 x 4.37 x 1.97 inch (151 x 111 x 50 mm).

      - Housing Material: ABS PA765, Flame Retardant, UL 94V-1.

      - Wiring:

        - Minimum 2.5mm2.

        - 75 Degrees C.

        - Tinned Copper.

      - Mounting:

        - Safe Zone.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C).

      - Storage: 32 to 122 Degrees F (0 to 50 Degrees C).

      - Audible Alarm: Internal greater than 65dB at 3.28-feet (1 m), quiet conditions.

    - Basis of Design: AGSLPGiS, Liquid Petroleum Gas Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: Detector i-S.

      - Target Gas: LPG, Liquid Petroleum Gas.

      - Power Consumption: Maximum 1.8W.

      - Power Rating: 12-24V AC or DC.

      - Size: 5.95 x 4.37 x 1.97 inch (151 x 111 x 50 mm).

      - Housing Material: ABS PA765, Flame Retardant, UL 94V-1.

      - Wiring:

        - Minimum 2.5mm2.

        - 75 Degrees C.

        - Tinned Copper.

      - Mounting:

        - Safe Zone.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C).

      - Storage: 32 to 122 Degrees F (0 to 50 Degrees C).

      - Audible Alarm: Internal greater than 65dB at 3.28-feet (1 m), quiet conditions.

** NOTE TO SPECIFIER ** Delete article if not required.

  - TFT DETECTORS

    - Basis of Design: AGSTFT, Gas Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: Merlin Gas Detector TFT

      - Target Gases:

        - Model NGTFT: Methane (CH4).

        - Model COTFT: Carbon Monoxide/

        - Model LPGTFT: Propane.

        - Model HTFT: Hydrogen.

        - Model O2TFT: Oxygen.

        - Model RTFT: Refrigerant.

      - Maximum Power Consumption: 90mA maximum at 24VDC.

      - DC Power: 12-32 VDC, nominal 24VDC.

      - Size: 5.51 x 3.74 x 1.18 inch (140 x 95 x 30 mm).

      - Housing Material: ABS PA765.

      - Wiring:

        - #15AWG Power Pair.

        - #18AWG Data Pair.

        - Tinned Copper.

      - Mounting:

        - Safe Zone.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RH, non-condensing.

      - Storage Temperature: Minus 13 to 122 Degrees F (Minus 25 to 50 Degrees C), up to 95 percent RH, non-condensing.

      - Audible Alarm: Greater than 70 dB at 3.28-feet (1 m), quiet conditions.

    - Basis of Design: AGSNGTFT, Natural Gas Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: Merlin Gas Detector TFT.

      - Target Gas: NG, Natural Gas.

      - Maximum Power Consumption: 90mA maximum at 24VDC.

      - DC Power: 12-32 VDC, nominal 24 VDC.

      - Size: 5.51 x 3.74 x 1.18 inch (140 x 95 x 30 mm).

      - Housing Material: ABS PA765.

      - Wiring:

        - #15AWG Power Pair.

        - #18AWG Data Pair.

        - Tinned Copper.

      - Mounting:

        - Safe Zone.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RH, non-condensing.

      - Storage Temperature: Minus 13 to 122 Degrees F (Minus 25 to 50 Degrees C), up to 95 percent RH, non-condensing.

      - Audible Alarm: Greater than 70 dB at 3.28-feet (1 m), quiet conditions.

    - Basis of Design: AGSAMOTFT, Ammonia (NH3) Gas Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: AGSAMOTFT.

      - Target Gas: NH3, Ammonia.

      - Voltage: 10 VDC - 30 VDC

      - Size: 8.5 x 5.5 x 4.25 inch (216 x 132 x 108 mm).

      - Housing J-Box: NEMA 4X, explosion proof, watertight, cast aluminum with O-ring seal and epoxy powder coat.

      - Controls: Magnet for calibration functions.

      - Operating: 14 to 104 Degrees F (Minus 10 to 40 Degrees C), 5-95 percent RH, non-condensing.

      - Alarm Indication: Visual LED's.

    - Basis of Design: AGSRTFT, Refrigerant Gas Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

** NOTE TO SPECIFIER ** Consult manufacturer's product data sheet to fill in the blank with the appropriate detectable gas identifier. A comprehensive chart is on page 1 of the product data sheet for this model..

      - Model: AGSRTFT - [___].

      - Target Gases: See manufacturer's product data sheet for table of detectable gases and part numbers.

      - Maximum Power Consumption: 90mA maximum at 24VDC.

      - DC Power: 12-32 VDC, nominal 24 VDC.

      - Size: 5.95 x 4.37 x 1.97 inch (151 x 111 x 50 mm).

      - Housing Material: ABS PA765.

      - Wiring:

        - #18-24AWG Power Pair.

        - #18-24AWG Data Pair.

        - Tinned Copper.

      - Mounting:

        - Mount 1-foot above finished floor.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RH, non-condensing.

      - Storage Temperature: Minus 13 to 122 Degrees F (Minus 25 to 50 Degrees C), up to 95 percent RH, non-condensing.

      - Audible Alarm: Greater than 95 dB at 3.28-feet (1 m), quiet conditions.

    - Basis of Design: AGSRTFT-PRO, Refrigerant Gas Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

** NOTE TO SPECIFIER ** Consult manufacturer's AGS Refrigerant Alarm Levels Section Sheet for the RTFT Detectors to fill in the blank with the appropriate detectable gas identifier.

      - Model: AGSRTFT-PRO - [___].

      - Target Gases: See manufacturer's product data sheet for table of detectable gases and part numbers.

      - Maximum Power Consumption: 90mA maximum at 24VDC.

      - DC Power: 12-32 VDC, nominal 24 VDC.

      - Size: 5.95 x 4.37 x 1.97 inch (151 x 111 x 50 mm).

      - Housing Material: ABS PA765.

      - Wiring:

        - #18-24AWG Power Pair.

        - #18-24AWG Data Pair.

        - Tinned Copper.

      - Mounting:

        - Mount 1-foot above finished floor.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RH, non-condensing.

      - Storage Temperature: Minus 13 to 122 Degrees F (Minus 25 to 50 Degrees C), up to 95 percent RH, non-condensing.

      - Audible Alarm: Greater than 95 dB at 3.28-feet (1 m), quiet conditions.

    - Basis of Design: AGSRTFT-LITE, Refrigerant Gas Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

** NOTE TO SPECIFIER ** Consult manufacturer's AGS Refrigerant Alarm Levels Section Sheet for the RTFT Detectors to fill in the blank with the appropriate detectable gas identifier.

      - Model: AGSRTFT-LITE - [___].

      - Target Gases: See manufacturer's product data sheet for table of detectable gases and part numbers.

      - Maximum Power Consumption: 90mA maximum at 24VDC.

      - DC Power: 12-32 VDC, nominal 24 VDC.

      - Size: 5.95 x 4.37 x 1.97 inch (151 x 111 x 50 mm).

      - Housing Material: ABS PA765.

      - Wiring:

        - #18-24AWG Power Pair.

        - #18-24AWG Data Pair.

        - Tinned Copper.

      - Mounting:

        - Mount 1-foot above finished floor.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RH, non-condensing.

      - Storage Temperature: Minus 13 to 122 Degrees F (Minus 25 to 50 Degrees C), up to 95 percent RH, non-condensing.

      - Audible Alarm: Greater than 95 dB at 3.28-feet (1 m), quiet conditions.

    - Basis of Design: AGSO2TFT, Oxygen Depletion/Enrichment Gas Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: Merlin Gas Detector TFT.

      - Target Gas: O2, Oxygen.

      - Maximum Power Consumption: 90mA maximum at 24VDC.

      - DC Power: 12-32 VDC, nominal 24 VDC.

      - Size: 5.51 x 3.74 x 1.18 inch (140 x 95 x 30 mm).

      - Housing Material: ABS PA765.

      - Wiring:

        - #15AWG Power Pair.

        - #18AWG Data Pair.

        - Tinned Copper.

      - Mounting:

        - Safe Zone.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RH, non-condensing.

      - Storage Temperature: Minus 13 to 122 Degrees F (Minus 25 to 50 Degrees C), up to 95 percent RH, non-condensing.

      - Audible Alarm: Greater than 70 dB at 3.28-feet (1 m), quiet conditions.

    - Basis of Design: AGLPGTFT, Liquid Petroleum Gas Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: Merlin Gas Detector TFT.

      - Target Gas: LPG, Liquid Petroelum Gas.

      - Maximum Power Consumption: 90mA maximum at 24VDC.

      - DC Power: 12-32 VDC, nominal 24 VDC.

      - Size: 5.51 x 3.74 x 1.18 inch (140 x 95 x 30 mm).

      - Housing Material: ABS PA765.

      - Wiring:

        - #15AWG Power Pair.

        - #18AWG Data Pair.

        - Tinned Copper.

      - Mounting:

        - Safe Zone.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RH, non-condensing.

      - Storage Temperature: Minus 13 to 122 Degrees F (Minus 25 to 50 Degrees C), up to 95 percent RH, non-condensing.

      - Audible Alarm: Greater than 70 dB at 3.28-feet (1 m), quiet conditions.

    - Basis of Design: AGSHTFT, Hydrogen Gas Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: Merlin Gas Detector TFT.

      - Target Gas: H, Hydrogen.

      - Maximum Power Consumption: 90mA maximum at 24VDC.

      - DC Power: 12-32 VDC, nominal 24 VDC.

      - Size: 5.51 x 3.74 x 1.18 inch (140 x 95 x 30 mm).

      - Housing Material: ABS PA765.

      - Wiring:

        - #15AWG Power Pair.

        - #18AWG Data Pair.

        - Tinned Copper.

      - Mounting:

        - Safe Zone.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RH, non-condensing.

      - Storage Temperature: Minus 13 to 122 Degrees F (Minus 25 to 50 Degrees C), up to 95 percent RH, non-condensing.

      - Audible Alarm: Greater than 70 dB at 3.28-feet (1 m), quiet conditions.

    - Basis of Design: AGSCOTFT, Carbon Monoxide Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: Merlin Gas Detector TFT.

      - Target Gas: CO, Carbon Monoxide.

      - Maximum Power Consumption: 90mA maximum at 24VDC.

      - DC Power: 12-32 VDC, nominal 24 VDC.

      - Size: 5.51 x 3.74 x 1.18 inch (140 x 95 x 30 mm).

      - Housing Material: ABS PA765.

      - Wiring:

        - #15AWG Power Pair.

        - #18AWG Data Pair.

        - Tinned Copper.

      - Mounting:

        - Safe Zone.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RH, non-condensing.

      - Storage Temperature: Minus 13 to 122 Degrees F (Minus 25 to 50 Degrees C), up to 95 percent RH, non-condensing.

      - Audible Alarm: Greater than 70 dB at 3.28-feet (1 m), quiet conditions.

    - Basis of Design: AGSCO2TFT, Carbon Dioxide Gas Detector as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: Merlin Gas Detector TFT.

      - Target Gas: CO2, Carbon Dioxide.

      - Maximum Power Consumption: 90mA maximum at 24VDC.

      - DC Power: 12-32 VDC, nominal 24 VDC.

      - Size: 5.51 x 3.74 x 1.18 inch (140 x 95 x 30 mm).

      - Housing Material: ABS PA765.

      - Wiring:

        - #15AWG Power Pair.

        - #18AWG Data Pair.

        - Tinned Copper.

      - Mounting:

        - Safe Zone.

        - Indoor Use.

        - Wall Mounted.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RH, non-condensing.

      - Storage Temperature: Minus 13 to 122 Degrees F (Minus 25 to 50 Degrees C), up to 95 percent RH, non-condensing.

      - Audible Alarm: Greater than 70 dB at 3.28-feet (1 m), quiet conditions.

** NOTE TO SPECIFIER ** Delete article if not required.

  - ISOLATION CONTROLLERS

    - Basis of Design: GDP2 Gas Detection System as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: GDP2 Gas Detection Controller.

      - Mounting: Wall mount.

      - Power Consumption: Maximum 20W, Full Load.

      - Power Voltage Input Range: 100-120VAC.

      - Gas Valve Output Range: 100-120VAC.

      - Terminal Wire Ratings: Copper 18AWG (0.75mm2), minimum 25 screw terminals.

      - Fuse: 3.15A.

      - Size: 5.51 x 7.48 x 2.44 inch (140 x 190 x 62 mm).

      - Housing Material: Polylac, PA765.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RF.

    - Basis of Design: GDP2X Advanced Gas Detection System as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: GDP2X Gas Detection Control Panel.

      - Mounting: Wall mount.

      - Power Consumption: Maximum 20W, Full Load.

      - Power Voltage Input Range: 100-120VAC.

      - Gas Valve Output Range: 100-120VAC.

      - Terminal Wire Ratings: Copper 18AWG (0.75mm2), minimum 25 screw terminals.

      - Fuse: 3.15A.

      - Size: 5.51 x 7.48 x 2.44 inch (140 x 190 x 62 mm).

      - Housing Material: Polylac, PA765.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RF.

    - Basis of Design: GDP4 Gas Detection System as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: GDP4 Gas Detection Controller.

      - Mounting: Wall mount.

      - Power Consumption: Maximum 20W, Full Load.

      - Power Voltage Input Range: 100-120VAC.

      - Gas Valve Output Range: 100-120VAC.

      - Terminal Wire Ratings: Copper 18AWG (0.75mm2), minimum 25 screw terminals.

      - Fuse: 3.15A.

      - Size: 7.08 x 10.03 x 3 inch (180 x 255 x 77 mm).

      - Housing Material: Polylac, PA765.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RF.

    - Basis of Design: AGSGDPX+ Advanced Gas Detection System as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: GDPX+ Gas Detection Control Panel.

      - Mounting: Wall mount.

      - Power Consumption: Maximum 48W, Full Load.

      - Power Voltage Input Range: 100-120VAC.

      - Gas Valve Output Range: 100-120VAC.

      - Electrical Contactor Output Range: 100-120VAC.

      - Communication: RS485 MODBUS RTU.

      - Terminal Wire Ratings: Copper 18AWG (0.75mm2), minimum 25 screw terminals.

      - Fuse: 3.15A.

      - Size: 7.08 x 10.03 x 3 inch (180 x 255 x 77 mm).

      - Housing Material: Polylac, PA765.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RF.

** NOTE TO SPECIFIER ** Delete article if not required.

  - VENTILATION CONTROLLERS

    - Basis of Design: MerlinGuard Gas Detection and Ventilation Control System as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: MerlinGuard Controller.

      - Mounting: Indoor use, wall mounting.

      - Power Consumption: Maximum 14.5W.

      - AC Power: 100-120V, 50/60Hz.

      - Wiring:

        - Power and Relay: #18-12AWG.

        - Detector: #12-18AWG Power Pair, #18-22AWG Data Pair.

        - Other: #18-22AWG.

      - Common Output: 24VDC Permanent, 0-10VDC Variable.

      - Size: 7.08 x 10.03 x 3 inch (180 x 255 x 77 mm).

      - Housing Material: Polylac, PA765, UL 94 V-1.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RH, non-condensing.

      - Storage Temperature: Minus 13 to 122 Degrees F (Minus 25 to 50 Degrees C), up to 95 percent RH, non-condensing.

      - Audible Alarm: Greater than 70 dB at 3.28-feet (1 m), quiet conditions.

      - For use with AGS TFT Detectors.

    - Basis of Design: AGSParkSafe Gas Detection and Ventilation Control System as manufactured and supplied by American Gas Safety; www.americangassafety.com .

      - Model: PARKSAFE Controller.

      - Mounting: Indoor use, wall mounting.

      - Power Consumption: Maximum 14.5W.

      - AC Power: 100-120V, 50/60Hz.

      - Wiring:

        - Power and Relay: #18-12AWG.

        - Detector: #12-18AWG Power Pair, #18-22AWG Data Pair.

        - Other: #18-22AWG.

      - Common Output: 24VDC Permanent, 0-10VDC Variable.

      - Size: 7.08 x 10.03 x 3 inch (180 x 255 x 77 mm).

      - Housing Material: Polylac, PA765, UL 94 V-1.

      - Operating: 14 to 122 Degrees F (Minus 10 to 50 Degrees C), 30 to 80 percent RH, non-condensing.

      - Storage Temperature: Minus 13 to 122 Degrees F (Minus 25 to 50 Degrees C), up to 95 percent RH, non-condensing.

      - Audible Alarm: Greater than 70 dB at 3.28-feet (1 m), quiet conditions.

** NOTE TO SPECIFIER ** Delete article if not required.

  - ACCESSORIES

    - Alarm Strobe Relay:

      - Size: 5.95 x 4.37 x 1.97 inch (151 x 111 x 50 mm).

      - Housing Material: ABS PA765. Flame Rating UL94 V-1.

      - Mounting:

        - Safe Zone.

        - Indoor Use.

        - Wall Mounted.

      - Visual Indicators: LED.

      - Power Consumption: 3W maximum without strobe.

      - AC Power: 100-120V, 50/60Hz.

      - Internal Fuse: Anti-Surge 3.15A, 250VAC.

      - Overvoltage Category: II.

      - Pollution Degree: 2.

      - Dry Contact Relay Output: 3x 1A switching current (resistive load) at 120VAC.

      - Wiring:

        - Minimum 18AWG.

        - 75 Degrees C.

        - Tinned Copper.

      - Product: AGSRGR Alarm Strobe Relay; www.americangassafety.com .

    - Fire Alarm Bypass:

      - Power Supply: 110-120VAC, 50/60HZ.

      - Enclosure:

        - Wall mount.

        - Flush mount.

      - Dimensions: 7-1/2 x 5-1/2 x 5-1/5 inch (191 x 140 x 127).

      - BAS Output: N/C COM N/O, Maximum 1A at 120VAC.

      - To Merlin Panel Terminals, Switched Connection: Dry Contact.

      - To Fire panel Terminals, Switched Connection: Dry Contact.

      - Product: AGS AGSFAB-1 Fire Alarm Bypass; www.americangassafety.com .

    - Two Double Pole / Double Throw Relay Pack:

      - Contact:

        - One pole 16A.

        - One form C (CO) or one form A (NO) contact.

      - Control Coil Type: DC, non-latching.

      - Coil Resistance: 360 Ohms.

      - Coil Contact: 5kV/10 mm coil-contact, reinforced insulation.

      - Ambient Temperature: 85 Degrees C.

      - Product: AGSRP2 Two Double Pole/Double Throw Relay Pack; www.americangassafety.com .

    - Audible Alarm Beacon:

      - Operating Voltage: 12VDC-24VDC.

      - Operating Current:

        - 0.42 at 12VDC.

        - 0.22A at 24VDC.

      - Operating Temperature: Minus 4 to 140 Degrees F.

      - Volume at 1-foot: High 105dB, Low 85dB.

      - Alarm Trigger: Trigger on Power.

      - Lens Tamper: N.C. 12VDC, 50mA Dry Contact.

      - IP Rating: IP54.

      - Product: AGSAAB Audible Alarm Beacon; www.americangassafety.com .

    - Detector Guard: 9-gauge steel wire cage with corrosion-resistant polyester coating.

      - Size: 7 x 5-3/4 x 4-1/2 inch (178 x 146 x 114 mm).

      - Product: AGS Detector Guard; www.americangassafety.com .

    - Water Resistant Cover:

      - Spacer: 8-1/2 x 6-1/2 x 4 inch (216 x 165 x 102 mm).

      - Product: AGSDETECTOR SPLASHGUARD Water Resistant Cover; www.americangassafety.com .

    - Calibration Test Gases:

      - Non-Reactive:

        - CO.

        - CH4 (Methane).

        - LPG.

        - H - Hydrogen.

        - O2 - Oxygen.

      - Reactive:

        - NO2.

      - Products:

        - Non-Reactive, Cylinder and Regulator; AGS-CAL-SIZE-KIT; www.americangassafety.com .

        - Reactive, Cylinder and Regulator; AGS-TEST-GAS-SIZE-KIT; www.americangassafety.com .

- EXECUTION

  - EXAMINATION

    - Do not begin installation until the substrates have been properly constructed and prepared.

    - If substrate preparation is the responsibility of another installer, notify Architect in writing of unsatisfactory preparation before proceeding.

  - PREPARATION

    - Clean surfaces thoroughly prior to installation.

    - Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

  - INSTALLATION

    - Install in accordance with manufacturer's instructions, approved submittals, and in proper relationship with adjacent construction.

  - FIELD QUALITY CONTROL

    - Field Inspection: Coordinate field inspection in accordance with appropriate sections in Division 01.

** NOTE TO SPECIFIER ** Include if manufacturer provides field quality control with onsite personnel for instruction or supervision of product installation, application, erection, or construction. Delete if not required.

    - Manufacturer's Services: Coordinate manufacturer's services in accordance with appropriate sections in Division 01.

  - CLEANING AND PROTECTION

    - Clean products in accordance with the manufacturer's recommendations.

    - Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION