SECTION 08 42 43

INTENSIVE CARE UNIT / CRITICAL CARE UNIT (ICU/CCU) ENTRANCES

Display hidden notes to specifier. (Don't know how? Click Here)

Copyright 2019 - 2026 ARCAT, Inc. - All rights reserved

** NOTE TO SPECIFIER ** ASSA ABLOY Entrance Systems; intensive care unit/ critical care unit (ICU/CCU) entrances.
This section is based on the products of ASSA ABLOY Entrance Systems, which is located at:
1900 Airport Rd.
Monroe, NC 28110
Toll Free Tel: 877-SPEC-123 
Fax: 704-290-5555
Email: request info (specdesk@besam-usa.com)
Web: https://www.assaabloyentrance.com/us/en/solutions/products/automatic-doors  

 [ Click Here ] for additional information.

ASSA ABLOY Entrance Systems is the world's most comprehensive supplier of entrance automation solutions. We take an integrative approach to the flow of people and goods, creating solutions with the best possible balance of cost, quality, and lifetime performance. At our disposal is a strong portfolio of well-established brands that have been the market leaders in their fields for decades to form a complete offering for the front, back and interior of your building.
For pedestrian door solutions, look to ASSA ABLOY Entrance Systems for a complete line of automatic sliding, swing, revolving, and manual ICU/CCU doors. Our products combine safety and security with comfort and convenience, making them a top choice for some of the most prestigious organizations in the retail, healthcare, hospitality, and transportation industries.
ASSA ABLOY Entrance Systems is dedicated to supporting the architect community. Contact the ASSA ABLOY Entrance Systems SPECDESK at 1-877-SPEC-123 or specdesk.na.aaes@assaabloy.com for application advice, plan review, and 3-part specification development. You may also visit our web site at assaabloyentrance.us to view our product line and access individual brand websites to download specifications and drawings.

- GENERAL

  - SECTION INCLUDES

** NOTE TO SPECIFIER ** Delete items below not required for project.

    - Intensive care unit/ critical care unit (ICU/CCU) entrance doors of the following types:

      - Manually operated sliding ICU/CCU entrances.

        - Smoke rated.

        - Non-smoke rated.

      - Manually operated swing ICU/CCU entrances.

        - Smoke rated.

        - Non-smoke rated.

      - Power operated swing ICU/CCU entrances.

      - Power operated sliding ICU/CCU entrances.

        - Smoke rated.

        - Non-smoke rated.

  - RELATED SECTIONS

** NOTE TO SPECIFIER ** Delete any sections below not relevant to this project; add others as required.

    - Section 07 90 00 - Joint Protection.

    - Section 08 42 29 - Automatic Entrances.

    - Section 08 42 29.33 - Swinging Automatic Entrances.

    - Section 08 83 13 - Mirrored Glass Glazing.

    - Division 7 Sections for caulking to the extent not specified in this section.

** NOTE TO SPECIFIER ** Delete if magnetic hold-open devices or power operated entrances are not required.

    - Divisions 16 - Electrical.

    - Division 26 and 28 Sections for connections to smoke/fire detection systems.

  - REFERENCES

** NOTE TO SPECIFIER ** Delete references from the list below that are not actually required by the text of the edited section.

    - Refer to the Referenced Standard's version year adopted by the Authorities Having Jurisdiction at the Project location.

    - American Architectural Manufacturers Association (AAMA):

      - AAMA 611 - Voluntary Specification for Anodized Architectural Aluminum.

    - American National Standards Institute (ANSI):

      - ANSI A117.1 - Accessible and Usable Buildings and Facilities.

      - ANSI Z97.1 - Standards for Safety Glazing Material Used in Buildings.

      - ANSI/BHMA A156.19 - Standards for Power Assist and Low Energy Power Operated Doors.

      - ANSI/BHMA A156.38 - American National Standard for Low Energy Power Operated Sliding and Folding Doors.

    - American Society for Testing and Materials (ASTM).

      - ASTM B221 Standard Specification for Aluminum and Aluminum Alloy Extruded Bars, Rods, Wire, Profiles and Tubes.

      - ASTM B209 Standard Specification for Aluminum and Aluminum Alloy Sheet and Plate.

    - International Code Council (ICC).

      - IBC: International Building Code Building Code.

      - CBC: California Building Code.

    - National Association of Architectural Metal Manufacturers (NAAMM):

      - Metal Finishes Manual for Architectural Metal Products.

    - National Fire Protection Association (NFPA):

      - NFPA 70 - National Electrical Code.

      - NFPA 101 - Life Safety Code.

      - NFPA 105 - Installation of Smoke Door Assemblies.

    - Underwriters Laboratories (UL):

      - UL 325 Standard for Safety for Door, Drapery, Gate, Louver and Window Operators and Systems.

      - UL 991 Listed - Tests for Safety-Related Controls Employing Solid-State Devices.

      - UL 1784 - Air Leakage Tests of Door Assemblies.

      - UL Listed R-9469 Fire Door Operator with Automatic Closer.

  - DEFINITIONS

** NOTE TO SPECIFIER ** Delete terms not referenced in this section.

    - Activation Device: Device that, when actuated, sends an electrical signal to the door operator to activate the operation of the door.

    - Knowing Act: Consciously initiating the opening of a power operated door using acceptable methods including wall mounted switches such as push plates and controlled access devices such as keypads, card readers and key switches.

    - Safety Device: A device that detects the presence of an object or person within a zone where contact could occur and provides a signal to stop the movement of the door.

  - PERFORMANCE REQUIREMENTS

** NOTE TO SPECIFIER ** Delete this section if power operated swing ICU/CCU entrances are not on this project.

    - Compliance with the following:

      - ANSI/BHMA A156.19 Standards for Power Assist and Low Energy Power Operated Doors.

      - Opening Force Requirements: Doors shall open with a manual force, not to exceed 30lbf (133N) to set the door in motion and 15 lbf to fully open the door applied at 1 inch (25 mm) from the latch edge of the door. The force required to prevent a stopped door from opening or closing shall not exceed 15 lbf (67 N) measured 1 inch (25 mm) from the latch edge of the door at any point during opening or closing.

      - Closing Time:

        - Doors shall be field adjustable to close from 90 degrees to 10 degrees in 3 seconds or longer as applicable per ANSI/BHMA A156.19 standards.

        - Doors shall be field adjusted to close from 10 degrees to fully closed in not less than 1.5 seconds.

** NOTE TO SPECIFIER ** Delete this section if power operated sliding ICU/CCU entrances are not on this project.

    - Compliance with the following:

      - ANSI/BHMA A156.38 American National Standard for Low Energy Power Operated Sliding and Folding Doors.

      - Entrapment Force Requirements:

        - Power Operated Sliding Doors: Not more than 15 lbf (67 N) required to prevent a stopped door from opening or closing.

        - Opening Time - Door(s) shall be adjusted to open at a speed of 12 inches per second maximum, from fully closed to fully open.

        - Closing Speed - Door(s) shall be adjusted to close at a speed of 6 inches per second maximum per leaf, from fully open to latch check.

** NOTE TO SPECIFIER ** Delete this section if MicroShield™ is not required.

    - MicroShield antimicrobial silver-based ion finish on all exposed surfaces including door pulls, door extrusions, rails and header to comply with the manufacturer's specified requirements.

      - Antimicrobial finish must permanently suppress the growth of bacteria, algae, fungus, mold and mildew.

  - SUBMITTALS

    - Submit under the provisions of Section 01 30 00.

    - Product Data:

      - Manufacturer's Data Sheets: Include installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions, and finishes.

      - Preparation instructions and recommendations.

      - Storage and handling requirements and recommendations.

      - Typical installation methods.

** NOTE TO SPECIFIER ** Delete selection samples if colors have already been selected.

    - Selection Samples: For each finish product specified, two complete sets of color chips representing manufacturer's full range of available colors and patterns.

    - Verification Samples: For each finish product specified, two samples, minimum size 6 inches (150 mm) square representing actual product, color, and patterns.

    - Shop Drawings: Include elevations, sections, and details, indicating dimensions, materials, and fabrication of doors, frames, sidelites, anchors, hardware, finish, options, and accessories. Include relationship with adjacent construction.

    - Informational Submittals: Manufacturer's product information and sustainability program credits available to contribute towards a LEED rated project certification.

      - Credit MR 4.1 and 4.2: Manufacturer's or fabricator's certificate indicating percentage of post-consumer recycled content by weight and pre-consumer recycled content by weight for each Product specified under this Section.

    - Manufacturers Field Reports: From an AAADM certified inspection technician and approval of doors for compliance with ANSI/BHMA A156.19 after installation completion.

    - Certified Test Reports: From UL, indicating doors are certified to UL 1784 - Air Leakage Test of Door Assemblies.

    - Manufacturer's Operating and Maintenance Manuals: Include spare parts list. For each item comprising the complete door opening installation in quantity as required in Division 01, Closeout Submittals. Manuals to include the name, address, and contact information of the manufacturer providing the entrance and their nearest service representatives. Deliver the final copies after successful testing of the completed installation.

    - Warranties and Maintenance: Special warranties and maintenance agreements specified in this Section.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: Company specializing in manufacturing products specified in this section with a minimum of ten (10) years' documented experience.

      - Manufacturer to have a company certificate issued by AAADM.

    - Installer Qualifications: Company specializing in performing Work of this section with minimum five (5) years documented experience with projects of similar scope and trained by Manufacturer.

    - Certified Inspector Qualifications: Certified by AAADM.

    - Source Limitations: Provide each type of product from a single manufacturing source to ensure uniformity.

    - Certifications: Operators are to be certified by the manufacturer to meet performance design criteria in accordance with the following standards.

      - ANSI/BHMA A156.19 American National Standard for Power Assist and Low Energy Operated Doors.

      - NFPA 101 - Life Safety Code.

      - UL 325 - Standard for Door, Drapery, Gate, Louver, and Window Operators and Systems.

    - Emergency Exit Door Requirements: Comply with requirements of authorities having jurisdiction for ICU/CCU entrances serving as a required means of egress.

  - PRE-INSTALLATION CONFERENCE

    - Convene a conference approximately two weeks before scheduled commencement of the Work. Attendees shall include Architect, Contractor and trades involved. The agenda shall include schedule, responsibilities, critical path items and approvals.

  - DELIVERY, STORAGE, AND HANDLING

    - Store and handle in strict compliance with manufacturer's written instructions and recommendations.

    - Protect from damage due to weather, excessive temperature, and construction operations.

  - PROJECT CONDITIONS

    - Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's recommended limits.

    - Field Measurements: Verify actual dimensions of openings to receive ICU/CCU entrances by field measurements before fabrication and indicate on shop drawings.

  - COORDINATION

    - Coordinate sizes and locations of recesses in concrete floors for recessed tracks and thresholds if applicable. Concrete work is specified in Division 03.

    - Electrical System Roughing-In: Coordinate layout and installation of power operated ICU/CCU entrances with connections to power supplies and access control system as applicable.

  - WARRANTY

    - Manufacturer's Warranty: Provide manufacturer's standard limited warranty.

    - General Warranty: Reference Division 01, General Requirements. Special warranties specified in this Article must not deprive Owner of other rights the Owner may have under other provisions of the Contract Documents and will be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

      - ICU/CCU Entrances: To be free of defects in material and workmanship for a period of one (1) year from the Date of Substantial Completion.

      - During Warranty Period:

        - A factory-trained technician will perform service and affect repairs. An inspection is to be performed after each adjustment or repair.

        - Warranty work, including emergency service, will be performed during normal business hours.

      - Emergency Call-Back Service: Manufacturer will have a dispatch procedure that shall be available 24 hours a Day, 7 Days a week for emergency call back service.

- PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer: ASSA ABLOY Entrance Systems, which is located at:
1900 Airport Rd.
Monroe, NC 28110
Toll Free Tel: 877-SPEC-123 
Fax: 704-290-5555
Email: request info (specdesk@besam-usa.com);Web: https://www.assaabloyentrance.com/us/en/solutions/products/automatic-doors

** NOTE TO SPECIFIER ** Delete one of the following two paragraphs: coordinate with requirements of Division 1 section on product options and substitutions.

    - Substitutions: Not permitted.

    - Requests for substitution and product approval in compliance with the specifications must be submitted in writing and in accordance with the procedures outlined in Division 1, Section "Substitution Procedures". Approval of requests is at the discretion of the architect, owner, and their designated consultants.

  - PERFORMANCE REQUIREMENTS

    - Smoke Rated ICU/CCU Doors: Certified by Underwriters Laboratories Inc. to UL 1784 - Air Leakage Tests of Door Assemblies.

    - Compliance with ANSI/BHMA A156.19 Standards for Power Assist and Low Energy Power Operated Doors.

    - ANSI/BHMA A156.38 American National Standard for Low Energy Power Operated Sliding and Folding Doors.

** NOTE TO SPECIFIER ** Delete article if not required.

  - MANUALLY OPERATED SLIDING ICU/CCU ENTRANCES

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 ICU/CCU Sliding Door Package, single slide, full breakout, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Manual.

      - Configuration: Single slide, two equal panel units; one operable leaf and one sidelite.

** NOTE TO SPECIFIER ** Delete if not required.

      - Smoke Rated: Certified to UL 1784.

** NOTE TO SPECIFIER ** Delete width not required.

      - Minimum Clear Door Opening Width: 41-1/2 inches (1054 mm) for 8 ft (2438 mm) unit width.

      - Minimum Clear Door Opening Width: 44-1/2 inches (1130 mm) for 8.5 ft (2591 mm) unit width.

      - Breakaway Capability: Sliding leaf and sidelite.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 ICU/CCU Sliding Door Package, single slide, fixed sidelite, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Manual.

      - Configuration: Single slide, two equal panel units; one operable leaf and one fixed sidelite.

** NOTE TO SPECIFIER ** Delete if not required.

      - Smoke Rated: Certified to UL 1784.

** NOTE TO SPECIFIER ** Delete width not required.

      - Minimum Clear Door Opening Width: 41-1/2 inches (1054 mm) for 8 ft (2438 mm) unit width.

      - Minimum Clear Door Opening Width: 44-1/2 inches (1130 mm) for 8.5 ft (2591 mm) unit width.

      - Breakaway Capability: Sliding leaf only.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 ICU/CCU Sliding Door Package, single slide, surface mounted, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Manual.

      - Configuration: Single slide unit without sidelite.

** NOTE TO SPECIFIER ** Delete if not required.

      - Smoke Rated: Certified to UL 1784.

** NOTE TO SPECIFIER ** Delete width not required.

      - Minimum Clear Door Opening Width: 41-1/2 inches (1054 mm) for 8 ft (2438 mm) unit width.

      - Minimum Clear Door Opening Width: 44-1/2 inches (1130 mm) for 8.5 ft (2591 mm) unit width.

      - Breakaway Capability: Sliding leaf.

      - Mounting: Surface mounted header installed on face of wall.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 ICU/CCU Sliding Door Package, bi-parting, full breakout, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Manual.

      - Configuration: Bi-parting, four equal panel units; two operable leaves and two sidelites.

** NOTE TO SPECIFIER ** Delete if not required.

      - Smoke Rated: Certified to UL 1784.

      - Breakaway Capability: Sliding leaves and sidelites.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 ICU/CCU Sliding Door Package, bi-parting, fixed sidelite, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Manual.

      - Configuration: Bi-parting, four equal panel units; two operable leaves and two fixed sidelites.

** NOTE TO SPECIFIER ** Delete if not required.

      - Smoke Rated: Certified to UL 1784.

      - Breakaway Capability: Sliding leaves only.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 ICU/CCU Sliding Door Package, bi-parting, surface mounted, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Manual.

      - Door Configuration: Bi-parting, two equal panel units and two operable leaves. No sidelites.

** NOTE TO SPECIFIER ** Delete if not required.

      - Smoke Rated: Certified to UL 1784.

      - Breakaway Capability: Sliding leaves.

      - Mounting: Surface mounted header installed on face of wall.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 ICU/CCU Telescopic Sliding Door Package, telescopic single slide, full breakout, ICU/CCU door system; manufactured by ASSA ABLOY.

      - Operation: Manual.

      - Configuration: Single slide, three equal panel units. Two operable leaves. One sidelite.

** NOTE TO SPECIFIER ** Keep for smoke rated entrance. Delete if not required.

      - Smoke Rated: Certified to UL 1784.

      - Breakaway Capability: Sliding leaves and sidelite.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 ICU/CCU Telescopic Sliding Door Package, telescopic single slide, fixed sidelite, ICU/CCU door system; manufactured by ASSA ABLOY.

      - Operation: Manual.

      - Door Configuration: Single slide, three equal panel units. Two operable leaves. One sidelite.

** NOTE TO SPECIFIER ** Keep for smoke rated entrance. Delete if not required.

      - Smoke Rated: Certified to UL 1784.

      - Breakaway Capability: Leading sliding leaf only.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 ICU/CCU Telescopic Sliding Door Package, telescopic bi-parting, full breakout, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Manual.

      - Door Configuration: Bi-parting, six equal panel units. Four operable leaves. Two sidelites.

** NOTE TO SPECIFIER ** Keep for smoke rated entrance. Delete if not required.

      - Smoke Rated: Certified to UL 1784.

      - Breakaway Capability: Sliding leaves and sidelites.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 ICU/CCU Telescopic Sliding Door Package, telescopic bi-parting, fixed sidelite, ICU/CCU door system; manufactured by ASSA ABLOY.

      - Operation: Manual.

      - Door Configuration: Bi-parting, six equal panel units. Four operable leaves. Two fixed sidelites.

** NOTE TO SPECIFIER ** Keep for smoke rated entrance. Delete if not required.

      - Smoke Rated: Certified to UL 1784.

      - Breakaway Capability: Leading sliding leaves only.

      - Mounting: Overhead header installed between jambs.

    - Stile and Rail Sliding Panels and Sidelites:

      - Material: Extruded Aluminum, Alloy 6063-T5 or 6063-T6.

      - Door Panels: 0.125 inch (3.2 mm) structural wall thickness including adjoining perimeter frames where applicable.

        - Aluminum Extrusions: Allow for a factory installed, slide-in type gasket.

      - Door Construction: By means of an integrated corner clip with 3/8 inch (9.5 mm) diameter all-thread through bolt from each stile.

        - Door Stiles Face: Flush with adjacent rails and muntin.

      - Glass Stops: 0.062 inch (1.58 mm) wall thickness. Provide security function as a standard by means of a fixed non-removable exterior section with glazing performed from the interior only.

** NOTE TO SPECIFIER ** Beveled glass stops available only with 1/4 inch glazing. Delete if not required.

        - Glass stops are to be beveled.

** NOTE TO SPECIFIER ** Delete vertical stiles option not required.

      - Vertical Stiles: Narrow stile, 2-1/8 inches (54 mm).

      - Vertical Stiles: Medium stile, 4 inches (102 mm).

** NOTE TO SPECIFIER ** Delete bottom rails options not required.

      - Bottom Rails: 4 inches (102 mm).

      - Bottom Rails: 7 inches (178 mm).

      - Bottom Rails: 10 inches (254 mm).

** NOTE TO SPECIFIER ** Intermediate muntin is required with integral blinds, but optional with other systems. Delete options not required.

      - Intermediate Muntin: 1-3/4 inches (45 mm).

      - Intermediate Muntin: 4 inches (102 mm).

** NOTE TO SPECIFIER ** Delete first gasketing option for smoke rated entrances. Delete the second option for non-smoke rated entrances.

      - Gasketing: Slide-in type, replaceable pile mohair seals.

        - Bottom Rails: Provided with a concealed adjustable sweep gasket.

      - Smoke Gasketing: Slide-in type, replaceable, smoke type gasket that is capable of withstanding 400 degrees F (204 degrees C) for 30 minutes.

        - Bottom Rails: Provided with a concealed adjustable sweep gasket capable of withstanding exposure to 400 degrees F (204 degrees C) for 30 minutes.

      - Glazing: Comply with ANSI Z97.1. Thickness as indicated.

** NOTE TO SPECIFIER ** Delete glazing types not required. If multiple types are required, add "Locations" to each.

        - Glazing: 1/4 inch (6 mm) tempered glass, unless otherwise specified.

        - Glazing: 5/8 inch (16 mm) insulated glass.

        - Glazing: 1 inch (25 mm) insulated glass.

        - Glazing: 1-1/4 inch (31 mm) insulated glass.

        - Glazing: Furnished by others.

** NOTE TO SPECIFIER ** Privacy glazing is optional and requires electrified power transfer option. Consult Manufacturer for additional information. Delete if not required.

        - Privacy Glazing Sliding Panels and Sidelite Panels: ASSA ABLOY InteGlass Switchable Privacy Glass: Electrified privacy film interlayer laminated between two pieces of clear 3/16 inch (5 mm) tempered glass panes.

          - Overall Thickness: 7/16 inch (11 mm).

          - Supplied with required bus bar, conductors, and nipple.

          - Films and Interlayers moisture Protection: Hermetically sealed edges.

          - Components/Electrical Connectors: Concealed and isolated from user.

          - Operation: Power On: Glass is clear. Power Off: Glass is opaque.

            - No electricity is consumed when glass is opaque.

          - Electrical:

            - Operating Voltage: 110 to 120 VAC / 50 to 60 Hz.

            - Operating Current: .012 Amps (12 mA per sq ft).

            - Power Consumption: Less than 1 watt per sq ft of privacy glass.

            - Surge protection module.

          - Electrical Devices and Connections: Wall switches, wiring, electrical splice boxes, connectors, and conduit according to Division 26 and 28 Sections.

          - Glazing Installation: Dry glazing. Wet glazing is not allowed.

            - See Division 8 Section "Glazing" for requirements and manufacturer instructions.

** NOTE TO SPECIFIER ** Consider a lower panel with opaque glazing when specifying integral blinds. Delete if not required.

        - Lower Lite Glazing Panels: Frosted insulating glass unit. Glass Lites: Interior and exterior; 1/4 inch (6 mm) tempered glass.

          - Overall Thickness: 1 inch (25 mm).

          - Frosted Glazing: Opaque, acid etched on No. 2 or No. 3 surface.

** NOTE TO SPECIFIER ** Consult manufacturer for integral blind information. Delete if not required.

        - Glazing Panels with Integral Blinds Sliding Panels and Sidelite Panels: Insulating glass units.

        - Glass Lites: Interior and exterior; 1/4 inch (6 mm) tempered glass.

        - Overall Thickness: 1-1/4 inch (31 mm).

** NOTE TO SPECIFIER ** Delete Locations option not required.

          - Locations: Upper lite only.

          - Locations: Upper and lower lite.

          - Locations: Full lite.

          - Integral Blinds: Blinds installed between glass lites.

            - Mechanically gear-driven tilt micro-blinds installed in sealed insulating glass units.

            - Internally mounted control assembly coupled to an external operator, controls the tilting of blind slats.

            - Tilt Operator: Thumb wheel. Dual control.

        - Glazing Installation: Dry glazing; wet glazing not allowed.

          - See manufacturer's instructions and Division 8 Section "Glazing" for requirements.

    - Sliding Panel Door Carriers: Manufacturer's standard carrier assembly that allows vertical adjustment:

      - Roller Wheels: Two heavy duty Delrin roller wheels per wheel assembly.

      - Wheels: Four roller wheels, 1-7/16 inch (36.5 mm) diameter, per active door leaf for operation over a replaceable aluminum track. Single journal with sealed oil impregnated bearings.

      - Two heavy duty self-aligning anti-risers per leaf.

** NOTE TO SPECIFIER ** Select below for single slide telescopic or bi-parting telescopic ICU/CCU entrances. Delete if not required.

    - Timing Transmission: Manufacturer's standard assembly that provides a smooth operation.

      - Sequences the opening of the first and second leaves to provide simultaneous opening of both leaves with a smooth operation; eliminating the "grabbing" that typically occurs with telescopic doors.

    - Framing Members: Provide ICU/CCU entrances as complete assemblies. Manufacturer's standard extruded aluminum framing reinforced as required to support loads.

** NOTE TO SPECIFIER ** Select first or second option below for single slide or bi-parting ICU/CCU entrances. Select third or fourth option for single telescopic or bi-parting telescopic ICU/CCU entrances. Delete Jambs options not required.

      - Vertical Jambs: 1-3/4 inches (44.5 mm) by 4-1/2 inches (114.3 mm).

      - Vertical Jambs: 1 inch (25.4 mm) by 4-1/2 inches (114.3 mm).

      - Vertical Jambs: 1-3/4 inches (44.5 mm) by 6 inches (152.4 mm).

      - Vertical Jambs: 1 inch (25.4 mm) by 6 inches (152.4 mm).

    - Extruded Aluminum Header: With replaceable aluminum track, mounted between the jambs and extending full width of entrance. Conceals door operators, carrier assemblies, and roller track, complete with hinged access panel for service and adjustment.

** NOTE TO SPECIFIER ** Headers to be anchored to overhead framing. Framing needs to be capable of supporting no less than 440 lbs. for single slide, 880 lbs. for bi-part or single slide telescopic. This provides a safety factor of double the weight of the door panel.

      - Header Capacity: Capable of supporting active breakout leaves up to 220 lb (100 kg) per leaf.

        - Headers to be anchored to overhead framing.

** NOTE TO SPECIFIER ** Paragraph below is for single slide or bi-parting ICU/CCU entrances. Delete if not required.

      - Header Size (WxH): 4-1/2 x 4-1/2 inches (114 x 114 mm).

** NOTE TO SPECIFIER ** Paragraph below is single slide telescopic or bi-parting telescopic ICU/CCU entrances. Delete if not required.

      - Header Size (WxH): 6 x 4-1/2 inches (152 x 114 mm).

** NOTE TO SPECIFIER ** Choose one of two gasketing options below. Delete "Gasketing" if entrances need to restrict smoke infiltration. Delete "Smoke Gasketing" if entrances do not need to restrict smoke infiltration.

      - Gasketing: Slide-in type, replaceable pile mohair seals.

      - Smoke Gasketing: Slide-in type, replaceable, smoke type gasket capable of withstanding 400 degrees F (204 degrees C) for 30 minutes.

      - Header Access: Continuous hinge at top of header allows cover to swing and allows complete access to operator and internal electronic and mechanical assemblies.

** NOTE TO SPECIFIER ** Entrance needs to be connected to the building ground for the following option - work by others. Delete if not required.

    - Anti-Static Grounding: Fabricate ICU/CCU entrances to be internally grounded to reduce static shock.

** NOTE TO SPECIFIER ** Electrified power transfer is required for privacy glass option. Delete if not required.

    - Electrified Power Transfer: Concealed from header to sliding and sidelite panels. Allows continuous power to sliding panels at all positions during sliding and breakout operations.

      - Rated at 5 amps (600 watts) at 120 VAC maximum.

      - Cable: 18 AWG stranded RoHS compliant UL listed 600 V cable with a temperature range of minus 58 to 194 degrees F (minus 50 to 90 degrees C), with a dynamic bend radius of 6X cable diameter and have a pull tension of 51 lbs. (23 kg) maximum. Withstand 8M cycles at rated dynamic bend radius.

    - Smoke Rated ICU/CCU Doors: Certified to UL 1784 - Air Leakage Test of Door Assemblies.

    - Hardware: Provide manufacturer's standard hardware as required for operation indicated.

      - Breakaway Arms and Bottom Pivot Assembly: Allow panels to break out to 90 degrees. Force to breakout sliding panel adjustable to maximum 50 lbf (222 N).

      - Nurse Assist Magnetic Catches: Retain breakout door and sidelite panels in the closed position.

** NOTE TO SPECIFIER ** Delete if not required.

      - Gas Regulated Damper: To control movement of breakout panels.

** NOTE TO SPECIFIER ** Centering wheel is available as an option for smoke rated entrances. Delete if not required.

      - Centering Wheel: To plumb the sliding panel in areas subject to moderate static pressure.

** NOTE TO SPECIFIER ** Latching hardware is standard for smoke rated entrances and optional for non-smoke rated entrances. Delete if not required.

      - Latching Hardware: Provided as indicated.

        - Positive Latch: Mortise type self-latching hookbolt, BHMA A156.5, Grade 1, with lever handles on each side.

          - Lever Style: End of lever to have a return towards door face.

** NOTE TO SPECIFIER ** Optional manual lock with keyed cylinder for non-smoke rated sliding ICU/CCU entrances. This option is not available for smoke rated entrances. Delete if not required.

      - Manual Lock and Keyed Cylinder: Mortise type lock with hook shaped deadbolt, BHMA A156.5, Grade 1.

** NOTE TO SPECIFIER ** The Adams Rite 4550 lever will reduce clear door opening when used on fixed sidelite entrances.

      - The Adams Rite 4550 lever is not available on bi-parting entrances.

      - C-shaped pull(s) required on sliding ICU/CCU entrances with manual lock and keyed cylinder.

      - Delete interior side and exterior side options not required.

        - Interior Side:

          - Thumbturn.

          - Keyed cylinder.

          - Adams-Rite 4550 lever.

          - Lock indicators shall be provided.

        - Exterior Side:

          - Keyed cylinder.

          - No cylinder.

** NOTE TO SPECIFIER ** Automatic releasing/latching is required with the full breakout trackless option. Delete if only the fixed sidelite is required or if full breakout with guide track is required.

      - Automatic Releasing/Latching: Concealed magnetic bolt allows breakout of sidelite panels when sliding panel is in full open position.

** NOTE TO SPECIFIER ** Recessed pull/C-shaped pull is provided standard on sliding ICU/CCU doors, not available with positive latching door hardware. Pulls are not an option for smoke rated entrances. Delete if not required.

      - Door Pulls: Provided as indicated.

** NOTE TO SPECIFIER ** Optional C-shaped pull required on exterior side of sliding ICU/CCU entrances with manual lock, keyed cylinder and 4550 lever.

      - Optional C-shaped pull required on both sides of sliding ICU/CCU entrances with manual lock, keyed cylinder and no lever.

        - Active Door Leaves Door Pulls:

          - Breakout Side: Manufacturer's Recessed Door Pull.

          - Non-Breakout Side: 10 inch (254 mm) C-shaped door pull.

            - Door Pull Mounting: Is not to decrease clear opening width.

        - Active Door Leaves Door Pulls:

          - Both Sides: Manufacturer's surface-mounted, 10 inch (254 mm) C-shaped door pull.

            - Door pull mounting shall not decrease clear opening width.

** NOTE TO SPECIFIER ** Self-closing device is optional for manually operated sliding ICU/CCU entrances. Delete if not required.

      - Self-Closing Device: Provided where indicated.

        - Non-electrified, adjustable speed, rack, and pinion mechanism.

          - Will close door to a positive latched position.

** NOTE TO SPECIFIER ** Optional magnetic hold-open device for ICU/CCU sliding entrances with optional self-closing device.

        - Magnetic Hold-Open Devices: Tied into the building fire alarm/sprinkler system. Upon receiving a signal, the device releases the self-closing sliding door leaf.

          - Accept 12 to 24 Vdc with no more current draw than 120 mA.

          - Hold Force: Not to exceed 30 lbs for manual door release.

      - Guide Track/Threshold: Manufacturer's threshold as indicated.

** NOTE TO SPECIFIER ** First option below is standard. Second option is available for full breakout entrance. Third option is standard for fixed sidelite models. Fourth options is standard for surface mount models. Delete options not required.

        - Full Breakout Trackless Design: Floor mounted guide track and threshold not allowed.

          - Breakout from a full open position only.

        - Full Breakout Entrance Guide Track: Floor mounted aluminum guide tracks adjacent to the sidelite portion of the sliding ICU/CCU entrance.

** NOTE TO SPECIFIER ** Select surface or recessed track. Delete option not required.

          - Surface mounted track.

          - Recessed mounted track.

          - Guide Track: Allows breakout from any position except when door is latched.

        - Fixed Sidelite Entrance Guide Track: Aluminum guide track integrated in the bottom of the sidelite portion of the sliding ICU/CCU entrance.

          - The guide track is to allow breakout from any position except when door is latched.

** NOTE TO SPECIFIER ** The following is not available for telescopic entrances.

        - Surface Mounted Entrance Guide Track: Aluminum fixed sidelite guide track mounted along the face of the wall. The track shall not extend past the jamb into the door opening.

          - Guide Track: Allow breakout from any position except when door is latched.

** NOTE TO SPECIFIER ** Delete article if not required.

  - MANUALLY OPERATED SWING ICU/CCU ENTRANCES

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 ICU/CCU Swing Door Package, swing ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Manual. Self-latching.

      - Door Configuration:

** NOTE TO SPECIFIER ** Delete configurations not required.

        - Unequal Pair of Swing Doors:

          - One Active Leaf: Primary panel.

          - One Inactive Leaf: Secondary panel.

        - Pair of Swing Doors: Two active leaves; both primary panels.

        - Single Swing Door: One active leaf; primary pane.

      - Minimum Clear Door Opening Width: As indicated on drawings.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 ICU/CCU Smoke Labeled, Swing Door Package, swing ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Manually operated, self-latching.

      - Smoke Rated: "S" Label, Certified to UL 1784.

      - Door Configuration:

** NOTE TO SPECIFIER ** Delete configurations not required.

        - Unequal Pair of Swing Doors:

          - One Active Leaf: Primary panel.

          - One Inactive Leaf: Secondary panel.

        - Pair of Swing Doors: Two active leaves; both primary panels.

        - Single Swing Door: One active leaf; primary pane.

      - Minimum Clear Door Opening Width: As indicated on drawings.

      - Mounting: Overhead header installed between jambs.

    - Stile and Rail Swing Panels and Sidelites:

      - Material: Extruded Aluminum, Alloy 6063-T5 or 6063-T6.

      - Door Panels: 0.125 inch (3.2 mm) structural wall thickness including adjoining perimeter frames where applicable.

        - Aluminum Extrusions: Allow for a factory installed, slide-in type gasket.

      - Door Construction: By means of an integrated corner clip with 3/8 inch (9.5 mm) diameter all-thread through bolt from each stile.

        - Face of Door Stiles: To be flush with adjacent rails and muntins.

      - Glass Stops: 0.062 inch (1.58 mm) wall thickness. Provide security function as a standard by means of a fixed non-removable exterior section with glazing to be performed from the interior only.

** NOTE TO SPECIFIER ** Beveled glass stops available only with 1/4 inch glazing. Delete if not required.

        - Glass stops are to be beveled.

** NOTE TO SPECIFIER ** Delete vertical stile size not required.

      - Vertical Stiles: Narrow stile, 2-1/8 inches (54 mm).

      - Vertical Stiles: Medium stile, 4 inches (102 mm).

** NOTE TO SPECIFIER ** Delete bottom rails size options not required.

      - Bottom Rails Size: 4 inches (102 mm).

      - Bottom Rails Size: 7 inches (178 mm).

      - Bottom Rails Size: 10 inches (254 mm).

** NOTE TO SPECIFIER ** Intermediate muntin is required with integral blinds, but optional with other systems. Delete options not required.

      - Intermediate Muntin: 1-3/4 inches (45 mm).

      - Intermediate Muntin: 4 inches (102 mm).

** NOTE TO SPECIFIER ** Delete "Gasketing" if entrances need to restrict smoke infiltration. Delete "Smoke Gasketing" if entrances do not need to restrict smoke infiltration.

      - Gasketing: Slide-in type, replaceable pile mohair seals.

        - Bottom Rails: Provided with a concealed adjustable sweep gasket.

      - Smoke Gasketing: Slide-in type, replaceable, smoke type gasket capable of withstanding 400 degrees F (204 degrees C) for 30 minutes.

        - Bottom Rails: Provided with a concealed adjustable sweep gasket capable of withstanding exposure to 400 degrees F (204 degrees C) for 30 minutes.

      - Glazing: Comply with ANSI Z97.1, thickness as indicated.

** NOTE TO SPECIFIER ** Delete glazing types not required. If multiple types are required, add "Locations" to each.

        - Glazing: 1/4 inch (6 mm) tempered glass, unless otherwise specified.

        - Glazing: 5/8 inch (16 mm) insulated glass.

        - Glazing: 1 inch (25 mm) insulated glass.

        - Glazing: 1-1/4 inch (31 mm) insulated glass.

        - Glazing: Furnished by others.

** NOTE TO SPECIFIER ** Consider a lower panel with opaque glazing when specifying integral blinds. Delete if not required.

        - Lower Lite Glazing Panels: 1 inch (25 mm) overall thickness frosted insulating glass unit consisting of an interior and exterior glass lite; both lites to be 1/4 inch (6 mm) tempered glass.

          - Frosted Glazing: Opaque, acid etched on No. 2 or No. 3 surface.

** NOTE TO SPECIFIER ** Consult manufacturer for integral blind information. Delete if not required.

        - Glazing Panels with Integral Blinds: 1-1/4 inch (31 mm) overall thickness insulating glass unit consisting of an interior and exterior glass lite; both lites to be 1/4 inch (6 mm) tempered glass.

** NOTE TO SPECIFIER ** Delete locations option not required.

          - Locations: Upper lite only.

          - Locations: Upper and lower lite.

          - Locations: Full lite.

          - Integral Blinds: Glass to have blinds installed between glass lites.

            - Mechanically gear-driven tilt micro-blind installed in the sealed insulating glass unit. Control Assembly: Internally mounted and coupled to the external operator, controls the tilting of blind slats.

            - Tilt Operator: Thumb wheel, dual control.

        - Installation: Dry glazing; wet glazing not allowed.

          - See manufacturer's instructions and Division 8 Section "Glazing" for requirements.

    - Framing Members: Provide ICU/CCU entrances as complete assemblies. Manufacturer's standard extruded aluminum framing reinforced as required to support loads.

** NOTE TO SPECIFIER ** Delete jambs option not required.

      - Vertical Jambs: 1-3/4 inches (44.5 mm) by 4-1/2 inches (114 mm).

      - Vertical Jambs: 1 inch (25 mm) by 4-1/2 inches (114 mm).

    - Extruded Aluminum Header: 0.109 inch (2.8 mm) structural wall thickness and extends the full width of entrance.

** NOTE TO SPECIFIER ** Select size required. Delete size not required.

      - Size (WxH): 4-1/2 x 4-1/2 inches (114 x 114 mm).

      - Size (WxH): 4-1/2 x 1-3/4 inches (114 x 44.5 mm).

** NOTE TO SPECIFIER ** Delete if not required.

    - Smoke Rated ICU/CCU Doors: Certified to UL 1784 - Air Leakage Tests of Door Assemblies.

    - Hardware: Manufacturer's standard hardware as required for operation indicated.

      - Hinges: Half mortise, gear type, continuous hinge; allows 180 degree swing.

** NOTE TO SPECIFIER ** Overhead stop is optional. Delete if not required.

      - Overhead Door Stops: Limit active doors from swinging past 90 degrees.

** NOTE TO SPECIFIER ** Door pulls for non-smoke rated doors only. Delete if not required.

      - Door Pulls: Manufacturer's surface-mounted, 10 inches (254 mm) C-shaped, door pull installed on both sides of active door leaves.

      - Latching Hardware: Provided as indicated.

** NOTE TO SPECIFIER ** Required latching for non-smoke rated active door leaves only. Delete if not required.

        - Active Door Leaves: Roller latch mounted in the top door rail.

** NOTE TO SPECIFIER ** Required latching for smoke rated active door leaves. Delete if not required.

        - Active Door Leaves: Concealed top and bottom vertical rods.

          - Bottom Rod: To serve as a counterbalance mechanism. Factory adjusted so it does not extend below the rail bottom:

          - Push Side: Push paddle.

          - Pull Side: Curved lever handle.

        - Inactive Leaf: Manual operated flush bolt.

** NOTE TO SPECIFIER ** Self-closing device is optional. Delete if not required.

      - Self-Closing Device: Provided as indicated.

        - Non-electrified, adjustable speed, surface mounted, rack and pinion door closer.

          - Will close door to a positive latched position.

          - Arm Type: Non-hold open.

          - Arm Type: Hold open.

          - Self-Closing Devices: Required on active door leaves only.

** NOTE TO SPECIFIER ** Delete magnetic hold-open device option if not required.

            - Magnetic Hold-Open Devices: Tied into the building fire alarm/sprinkler system. Upon receiving a signal, the device releases the self-closing sliding door leaf.

          - Accept 12 to 24 Vdc with no more current draw than 120 mA.

          - Hold Force: Not to exceed 30 lbs for manual door release.

** NOTE TO SPECIFIER ** Delete article if not required.

  - POWER OPERATED SWING ICU/CCU ENTRANCES

    - Performance Requirements.

      - Compliant with ANSI/BHMA A156.19 Standards for Power Assist and Low Energy Power Operated Doors.

    - Basis of Design: VersaMax 2.0 ICU/CCU Swing Door Package, swing ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Power open and close. Self-latching.

      - Door Configuration:

** NOTE TO SPECIFIER ** Delete configurations not required.

        - Unequal Pair of Swing Doors:

          - One Active Leaf: Primary panel.

          - One Inactive Leaf: Secondary panel.

        - Pair of Swing Doors: Two active leaves; both primary panels.

        - Single Swing Door: One active leaf; primary pane.

      - Mounting: Overhead header installed between jambs.

    - Stile and Rail Swing Panels and Sidelites:

      - Material: Extruded Aluminum, Alloy 6063-T5 or 6063-T6.

      - Door Panels: 0.125 inch (3.2 mm) structural wall thickness including adjoining perimeter frames where applicable.

        - Aluminum Extrusions: Allow for a factory installed, slide-in type gasket.

      - Door Construction: By means of an integrated corner clip with 3/8 inch (9.5 mm) diameter all-thread through bolt from each stile.

        - Face of Door Stiles: To be flush with adjacent rails and muntins.

      - Glass Stops: 0.062 inch (1.58 mm) wall thickness. Provide security function as a standard by means of a fixed non-removable exterior section with glazing to be performed from the interior only.

** NOTE TO SPECIFIER ** Beveled glass stops available only with 1/4 inch glazing. Delete if not required.

        - Glass stops are to be beveled.

** NOTE TO SPECIFIER ** Delete vertical stile size not required.

      - Vertical Stiles: Narrow stile, 2-1/8 inches (54 mm).

      - Vertical Stiles: Medium stile, 4 inches (102 mm).

** NOTE TO SPECIFIER ** Delete bottom rails size options not required.

      - Bottom Rails Size: 4 inches (102 mm).

      - Bottom Rails Size: 7 inches (178 mm).

      - Bottom Rails Size: 10 inches (254 mm).

** NOTE TO SPECIFIER ** Intermediate muntin is required with integral blinds, but optional with other systems. Delete options not required.

      - Intermediate Muntin: 1-3/4 inches (45 mm).

      - Intermediate Muntin: 4 inches (102 mm).

      - Gasketing: Slide-in type, replaceable pile mohair seals.

        - Bottom Rails: Provided with a concealed adjustable sweep gasket.

      - Glazing: Comply with ANSI Z97.1, thickness as indicated.

** NOTE TO SPECIFIER ** Delete glazing types not required. If multiple types are required, add "Locations" to each.

        - Glazing: 1/4 inch (6 mm) tempered glass, unless otherwise specified.

        - Glazing: 5/8 inch (16 mm) insulated glass.

        - Glazing: 1 inch (25 mm) insulated glass.

        - Glazing: 1-1/4 inch (31 mm) insulated glass.

        - Glazing: Furnished by others.

** NOTE TO SPECIFIER ** Consider a lower panel with opaque glazing when specifying integral blinds. Delete if not required.

        - Lower Lite Glazing Panels: 1 inch (25 mm) overall thickness frosted insulating glass unit consisting of an interior and exterior glass lite; both lites to be 1/4 inch (6 mm) tempered glass.

          - Frosted Glazing: Opaque, acid etched on No. 2 or No. 3 surface.

** NOTE TO SPECIFIER ** Consult manufacturer for integral blind information. Delete if not required.

        - Glazing Panels with Integral Blinds: 1-1/4 inch (31 mm) overall thickness insulating glass unit consisting of an interior and exterior glass lite; both lites to be 1/4 inch (6 mm) tempered glass.

** NOTE TO SPECIFIER ** Delete locations option not required.

          - Locations: Upper lite only.

          - Locations: Upper and lower lite.

          - Locations: Full lite.

          - Integral Blinds: Glass to have blinds installed between glass lites.

            - Mechanically gear-driven tilt micro-blind installed in the sealed insulating glass unit. Control Assembly: Internally mounted and coupled to the external operator, controls the tilting of blind slats.

            - Tilt Operator: Thumb wheel, dual control.

        - Installation: Dry glazing; wet glazing not allowed.

          - See manufacturer's instructions and Division 8 Section "Glazing" for requirements.

    - Framing Members: Provide ICU/CCU entrances as complete assemblies. Manufacturer's standard extruded aluminum framing reinforced as required to support loads.

** NOTE TO SPECIFIER ** Delete jambs option not required.

      - Vertical Jambs: 1-3/4 inches (44.5 mm) by 4-1/2 inches (114 mm).

      - Vertical Jambs: 1 inch (25 mm) by 4-1/2 inches (114 mm).

    - Extruded Aluminum Header: 0.109 inch (2.8 mm) structural wall thickness and extends the full width of entrance.

** NOTE TO SPECIFIER ** Select size required. Delete size not required.

      - Size (WxH): 4-1/2 x 4-1/2 inches (114 x 114 mm).

      - Size (WxH): 4-1/2 x 1-3/4 inches (114 x 44.5 mm).

    - Hardware: Manufacturer's standard hardware as required for operation indicated.

      - Hinges: Half mortise, gear type, continuous hinge; allows 180 degree swing.

      - Door Pulls: Manufacturer's surface-mounted, 10 inches (254 mm) C-shaped, door pull installed on both sides of active door leaves.

      - Latching Hardware: Provided as indicated.

        - Active Door Leaves: Roller latch mounted in the top door rail.

        - Inactive Leaf: Manual operated flush bolt.

    - Low Energy Door Operator:

      - Basis of Design: ASSA ABLOY SW100 low energy automatic door operator.

      - Reference Standard: ANSI/BHMA A156.19.

      - Configuration: Operator to control single swinging doors and pairs of swinging doors as indicated on the drawings and specified below:

        - Pairs of Doors: Simultaneous swing; leaves active.

      - Automatic Door Operator: Electro-mechanical, non-handed operator, powered by 24 volt, 1/8 hp motor. Adjustable Spring: Compensates for different manual push forces required on varying door widths.

        - Operate and control doors up to 200 lbs (91 kg) and 48 inch (1219 mm) wide.

        - Surface Mounted Operator:

          - Side Access Operator Housing (Depth x Height): 5-1/8 x 4-5/16 inches (130 x 110 mm).

            - Housing Material: Extruded aluminum with removable cover.

          - Surface Mounted Housing: Continuous for full width of door.

          - Connecting Hardware: A steel arm from the operator, mounted to the top face of the swing door.

          - UL Listed R-9469 Fire Door Operator with Automatic Closer; surface mounted operator.

        - Operator Temperature Range: Minus 20 to 160 degrees F (Minus 29 to 71 degrees C).

        - Electrical Characteristics: Built-in thermal overload protection.

          - Nominal Current Draw: 75 watts, 0.625 amps at 120 VAC.

** NOTE TO SPECIFIER ** Battery convenience mode is optional. Delete if not required.

        - Battery Convenience Mode: Operator maintains continuous operation by battery power during power failure. Battery to be continuously monitored and provides a warning signal if the battery is not working properly.

      - Door Operation:

        - Opening Cycle: Adjustable speed operator controls the door opening to the back check position, where the opening speed is reduced.

          - Manual Door Operation: Operational forces of 15 lbf (67 N) to fully open the door applied at 1 inch (25 mm) from the latch edge of the door.

        - Hold Open: Operator stops and holds the door open at the selected door opening angle for an adjustable period of time (1.5 to 30 seconds).

        - Closing Cycle: Power closing by clock spring and motor. The door will slow to low speed at latch check before reaching the fully closed position.

        - Electronic Dampening System: Automatically counteracts additional forces applied to the door during the opening or closing cycle by reducing door speed.

        - Stack Pressure Compensation: Allows for increases of forces to overcome minor stack pressures while compensating to lower manual push forces when the door is used in manual mode in order to comply with ANSI/BHMA A156.19.

        - Obstruction Control: Stops and reverses door movement.

        - Astragal Coordinator: Sequenced electronic operation between operators for pairs of doors allowing astragal coordination.

        - Lock Retry Circuit: If attempt to fully close the door is unsuccessful, the operator automatically reverse opens 10 degrees and reclose in an attempt to successfully close the door.

        - Electronic Controls: Microprocessor controlled unit controls the operation and switching of the swing power operator.

          - Microprocessor Unit: Low voltage power supply for all means of actuation.

          - Controls include a time delay from 1.5 to 30 seconds for a normal cycle.

        - Control Switch: Equipped with the following type of multi-position function switch:

** NOTE TO SPECIFIER ** Delete rocker switch option not required.

          - Rocker Switch: 3 position. Mounted on end cap (On-Off-Hold).

          - Rocker Switch: 2 position. Mounted on end cap (On-Off).

** NOTE TO SPECIFIER ** Operator interface below is optional. Delete if not required.

      - Operator Interface: Safety Sensor Integration for overhead presence safety device and door mounted reactivation safety sensors.

    - Activation and Safety Control Devices: Provide in accordance with ANSI/BHMA standards, for condition of exposure and long-term maintenance-free operation under normal traffic load for occupancy type indicated. Coordinate activation and safety devices with door operation and door operator mechanisms.

** NOTE TO SPECIFIER ** Select the type of activation and safety devices required. Delete option not required.

      - Knowing Act Activation Device:

        - Push Plate: Hard wired, 4-1/2 inch (114 mm) square stainless steel push plate switches engraved with "Push to Open" with a blue ADA logo.

        - Push Plate: Hard wired, 6 inch (152 mm) round stainless steel push plate switches engraved with "Push to Open" with a blue ADA logo.

        - Push Plate: Jamb mounted, hard wired, 1-1/2 x 4-3/4 inch (38 x 121 mm), stainless steel push plate switches engraved with "Push to Open" with a blue ADA logo.

        - Push Plate: Radio controlled, wireless, 4-1/2 inch (114 mm) square stainless steel push plate switches engraved with "Push to Open" with a blue ADA logo.

        - Push Plate: Radio controlled, wireless, 6 inch (152 mm) round stainless steel push plate switches engraved with "Push to Open" with a blue ADA logo.

        - Sensor Plate: Touchless, 2-3/4 x 4-1/2 inch (79 x 114 mm) activation senor plates, black polycarbonate with white letters. Microwave technology has an adjustable range of 4 to 24 inches (51 x 610 mm).

        - Sensor Plate: Touchless, 4-1/2 inch (114 mm) square activation senor plates, black polycarbonate with white letters. Microwave technology has an adjustable range of 4 to 24 inches (51 x 610 mm).

      - Manual Operation:

        - Power assist function to provide ease of manual operational forces.

          - Manual Push Force: Not to exceed 15 lbf (67 N) maximum.

        - Programmable to provide a "push and go" feature allowing door to open automatically if pulled or pushed open manually.

** NOTE TO SPECIFIER ** Safety sensors are not required by ANSI/BHMA A156.19 for low-energy operators. Delete if not required.

      - Safety Devices:

        - Door Mounted Presence Sensor (DMPS): ASSA ABLOY door mounted infrared presence safety device, mounted at top of each door. Adjustable to provide detection field sizes and functions required.

          - Provide detection during door travel.

          - Upon Detection: Provide a signal to stop or reverse the door action.

        - Door Mounted Safety Sensor Devices: Door mounted as specified.

** NOTE TO SPECIFIER ** Select one of the following mounting options for door mounted safety sensor devices. Delete options not required.

          - Mounting: On the swing (pull) side and the approach (push) side of the door. 2 safety sensors per leaf. Provides detection on sides of the door.

          - Mounting: On the swing (pull) side of the door. 1 safety sensor per leaf. Provides detection on one side of the door only.

          - Mounting: On approach (push) side of the door. 1 safety sensor per leaf. Provides detection on one side of the door only.

          - Power transfer from the door mounted safety sensor to operator is to be through an exposed door cord.

** NOTE TO SPECIFIER ** Delete if not required.

  - POWER OPERATED, SLIDING ICU/CCU ENTRANCES

    - Performance Requirements:

      - Compliant with ANSI/BHMA A156.38.

      - Smoke Rated ICU/CCU Doors: Certified by Underwriters Laboratories Inc. to UL 1784 - Air Leakage Test of Door Assemblies.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 Touchless ICU/CCU Sliding Door Package, single slide, full breakout, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Power operated open and close cycle; opening cycle activated by "knowing act activation".

      - Door Configuration: Single slide, two equal panel unit with one operable leaf and one sidelite.

** NOTE TO SPECIFIER ** Delete if not required.

      - Smoke Rated: Certified to UL 1784.

** NOTE TO SPECIFIER ** Delete width option not required.

      - Minimum Clear Door Opening Width: 41-1/2 inches (1054 mm) for 8 ft (2438 mm) unit width.

      - Minimum Clear Door Opening Width: 44-1/2 inches (1130 mm) for 8.5 ft (2591 mm) unit width.

      - Breakaway Capability: Sliding leaf and sidelite.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 Touchless ICU/CCU Sliding Door Package, single slide, fixed sidelite, ICU/CCU door system as manufactured by ASSA ABLOY.

      - Operation: Power operated open and close cycle; opening cycle activated by "knowing act activation".

      - Door Configuration: Single slide, two equal panel unit with one operable leaf and one fixed sidelite.

** NOTE TO SPECIFIER ** Delete if not required.

      - Smoke Rated: Certified to UL 1784.

** NOTE TO SPECIFIER ** Delete width not required.

      - Minimum Clear Door Opening Width: 41-1/2 inches (1054 mm) for 8 ft (2438 mm) unit width.

      - Minimum Clear Door Opening Width: 44-1/2 inches (1130 mm) for 8.5 ft (2591 mm) unit width.

      - Breakaway Capability: Sliding leaf only.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 Touchless ICU/CCU Sliding Door Package, single slide, surface mounted, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Power operated open and close cycle; opening cycle activated by "knowing act activation".

      - Door Configuration: Single slide unit without sidelite.

** NOTE TO SPECIFIER ** Delete if not required.

      - Smoke Rated: Certified to UL 1784.

** NOTE TO SPECIFIER ** Delete width not required.

      - Minimum Clear Door Opening Width: 41-1/2 inches (1054 mm) for 8 ft (2438 mm) unit width.

      - Minimum Clear Door Opening Width: 44-1/2 inches (1130 mm) for 8.5 ft (2591 mm) unit width.

      - Breakaway Capability: Sliding leaf.

      - Mounting: Surface mounted header installed on face of wall.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 Touchless ICU/CCU Sliding Door Package, bi-parting, full breakout, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Power operated open and close cycle; opening cycle activated by "knowing act activation".

      - Door Configuration: Bi-parting, four equal panel unit with two operable leaves and two sidelites.

      - Breakaway Capability: Sliding leaves and sidelites.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 Touchless ICU/CCU Sliding Door Package, bi-parting, fixed sidelite, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Power operated open and close cycle; opening cycle activated by "knowing act activation".

      - Door Configuration: Bi-parting, four equal panel unit with two operable leaves and two fixed sidelites.

      - Breakaway Capability: Leading sliding leaves only.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 Touchless ICU/CCU Sliding Door Package, bi-parting, surface mounted, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Power operated open and close cycle; opening cycle activated by "knowing act activation".

      - Door Configuration: Bi-parting, two equal panel unit with two operable leaves and no sidelites.

      - Breakaway Capability: Sliding leaves only.

      - Mounting: Surface mounted header installed on face of wall.

    - Basis of Design: VersaMax 2.0 Touchless ICU/CCU Telescopic Sliding Door Package, telescopic, single slide, full breakout, ICU/CCU door system as manufactured by ASSA ABLOY.

      - Operation: Power operated open and close cycle; opening cycle activated by "knowing act activation".

** NOTE TO SPECIFIER ** Delete if not required.

      - Smoke Rated: Certified to UL 1784.

      - Door Configuration: Single slide, three equal panel unit with two operable leaves and one sidelite.

      - Breakaway Capability: Sliding leaves and sidelite.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 Touchless ICU/CCU Telescopic Sliding Door Package, telescopic, single slide, fixed sidelite, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Power operated open and close cycle; opening cycle activated by "knowing act activation".

** NOTE TO SPECIFIER ** Delete if not required.

      - Smoke Rated: Certified to UL 1784.

      - Door Configuration: Single slide, three equal panel unit with two operable leaves and one fixed sidelite.

      - Breakaway Capability: Leading sliding leaf only.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 Touchless ICU/CCU Telescopic Sliding Door Package, telescopic, bi-parting, full breakout, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Power operated open and close cycle; opening cycle activated by "knowing act activation".

      - Door Configuration: Bi-parting, six equal panel unit with four operable leaves and two sidelites.

      - Breakaway Capability: Sliding leaves and sidelites.

      - Mounting: Overhead header installed between jambs.

** NOTE TO SPECIFIER ** Delete if not required.

    - Basis of Design: VersaMax 2.0 Touchless ICU/CCU Telescopic Sliding Door Package, telescopic, bi-parting, fixed sidelite, ICU/CCU door system; as manufactured by ASSA ABLOY.

      - Operation: Power operated open and close cycle; opening cycle activated by "knowing act activation".

      - Door Configuration Bi-parting, six equal panel unit with four operable leaves and two fixed sidelites.

      - Breakaway Capability: Leading sliding leaves only.

      - Mounting: Overhead header installed between jambs.

    - Stile and Rail Sliding Panels and Sidelites:

      - Material: Extruded Aluminum, Alloy 6063-T5 or 6063-T6.

      - Door Panels: 0.125 inch (3 mm) structural wall thickness including adjoining perimeter frames where applicable.

        - Aluminum Extrusions: Allow for a factory installed, slide-in type gasket.

      - Door Construction: By means of an integrated corner clip with 3/8 inch (9.5 mm) diameter all-thread through bolt from each stile.

        - Face of Door Stiles: Flush with adjacent rails and muntin.

      - Glass Stops: 0.062 inch (1.6 mm) wall thickness and provide security function as a standard by means of a fixed non-removable exterior section with glazing to be performed from the interior only.

** NOTE TO SPECIFIER ** Beveled glass stops available only with 1/4 inch glazing. Delete if not required.

        - Glass stops are to be beveled.

** NOTE TO SPECIFIER ** Delete vertical stiles option not required.

      - Vertical Stiles: Narrow stile, 2-1/8 inches (54 mm).

      - Vertical Stiles: Medium stile, 4 inches (102 mm).

** NOTE TO SPECIFIER ** Delete bottom rails options not required.

      - Bottom Rails: 4 inches (102 mm).

      - Bottom Rails: 7 inches (178 mm).

      - Bottom Rails: 10 inches (254 mm).

** NOTE TO SPECIFIER ** Intermediate muntin is required with integral blinds, but optional with other systems. Delete options not required.

      - Intermediate Muntin: 1-3/4 inches (45 mm).

      - Intermediate Muntin: 4 inches (102 mm).

** NOTE TO SPECIFIER ** Delete first gasketing option for smoke rated entrances. Delete the second option for non-smoke rated entrances.

      - Gasketing: Slide-in type, replaceable pile mohair seals.

        - Bottom Rails: Provided with a concealed adjustable sweep gasket.

      - Smoke Gasketing: Slide-in type, replaceable, smoke type gasket that is capable of withstanding 400 degrees F (204 degrees C) for 30 minutes.

        - Bottom Rails: Provided with a concealed adjustable sweep gasket capable of withstanding exposure to 400 degrees F (204 degrees C) for 30 minutes.

      - Glazing: Comply with ANSI Z97.1. Thickness as indicated.

** NOTE TO SPECIFIER ** Delete glazing types not required. If multiple types are required, add "Locations" to each.

        - Glazing: 1/4 inch (6 mm) tempered glass, unless otherwise specified.

        - Glazing: 5/8 inch (16 mm) insulated glass.

        - Glazing: 1 inch (25 mm) insulated glass.

        - Glazing: 1-1/4 inch (31 mm) insulated glass.

        - Glazing: Furnished by others.

** NOTE TO SPECIFIER ** Privacy glazing is optional and requires electrified power transfer option. Consult Manufacturer for additional information. Delete if not required.

        - Privacy Glazing Sliding Panels and Sidelite Panels: ASSA ABLOY InteGlass Switchable Privacy Glass: Electrified privacy film interlayer laminated between two pieces of clear 3/16 inch (5 mm) tempered glass panes.

          - Overall Thickness: 7/16 inch (11 mm).

          - Supplied with required bus bar, conductors, and nipple.

          - Films and Interlayers moisture Protection: Hermetically sealed edges.

          - Components/Electrical Connectors: Concealed and isolated from user.

          - Operation: Power On: Glass is clear. Power Off: Glass is opaque.

            - No electricity is consumed when glass is opaque.

          - Electrical:

            - Operating Voltage: 110 to 120 VAC / 50 to 60 Hz.

            - Operating Current: .012 Amps (12 mA per sq ft).

            - Power Consumption: Less than 1 watt per sq ft of privacy glass.

            - Surge protection module.

          - Electrical Devices and Connections: Wall switches, wiring, electrical splice boxes, connectors, and conduit according to Division 26 and 28 Sections.

          - Glazing Installation: Dry glazing. Wet glazing is not allowed.

            - See Division 8 Section "Glazing" for requirements and manufacturer instructions.

        - Lower Lite Glazing Panels: Frosted insulating glass unit. Glass Lites: Interior and exterior; 1/4 inch (6 mm) tempered glass.

          - Overall Thickness: 1 inch (25 mm).

          - Frosted Glazing: Opaque, acid etched on No. 2 or No. 3 surface.

** NOTE TO SPECIFIER ** Consult manufacturer for integral blind information. Delete if not required.

        - Glazing Panels with Integral Blinds Sliding Panels and Sidelite Panels: Insulating glass units.

        - Glass Lites: Interior and exterior; 1/4 inch (6 mm) tempered glass.

        - Overall Thickness: 1-1/4 inch (31 mm).

** NOTE TO SPECIFIER ** Delete Locations option not required.

          - Locations: Upper lite only.

          - Locations: Upper and lower lite.

          - Locations: Full lite.

          - Integral Blinds: Blinds installed between glass lites.

            - Mechanically gear-driven tilt micro-blinds installed in sealed insulating glass units.

            - Internally mounted control assembly coupled to an external operator, controls the tilting of blind slats.

            - Tilt Operator: Thumb wheel. Dual control.

        - Glazing Installation: Dry glazing; wet glazing not allowed.

          - See manufacturer's instructions and Division 8 Section "Glazing" for requirements.

    - Sliding Panel Door Carriers: Manufacturer's standard carrier assembly that allows vertical adjustment:

      - Roller Wheels: Two heavy duty Delrin roller wheels per wheel assembly.

      - Wheels: Four roller wheels, 1-7/16 inch (36.5 mm) diameter, per active door leaf for operation over a replaceable aluminum track. Single journal with sealed oil impregnated bearings.

      - Two heavy duty self-aligning anti-risers per leaf.

** NOTE TO SPECIFIER ** Select below for single slide telescopic or bi-parting telescopic ICU/CCU entrances. Delete if not required.

    - Timing Transmission: Manufacturer's standard assembly that provides a smooth operation.

      - Sequences the opening of the first and second leaves to provide simultaneous opening of both leaves with a smooth operation; eliminating the "grabbing" that typically occurs with telescopic doors.

    - Framing Members: Provide ICU/CCU entrances as complete assemblies. Manufacturer's standard extruded aluminum framing reinforced as required to support loads.

** NOTE TO SPECIFIER ** Select below for single slide or bi-parting ICU/CCU entrances. Delete if not required.

      - Vertical Jambs: 1-3/4 inches (44.5 mm) by 4-1/2 inches (114 mm).

** NOTE TO SPECIFIER ** Select below for single slide telescopic or bi-parting telescopic ICU/CCU entrances. Delete if not required.

      - Vertical Jambs: 1-3/4 inches (44.5 mm) by 6 inches (152.4 mm).

    - Extruded Aluminum Header: With replaceable aluminum track, mounted between the jambs and extending full width of entrance. Conceals door operators, carrier assemblies, and roller track, complete with hinged access panel for service and adjustment.

** NOTE TO SPECIFIER ** Headers to be anchored to overhead framing. Framing needs to be capable of supporting no less than 440 lbs. for single slide, 880 lbs. for bi-part or single slide telescopic. This provides a safety factor of double the weight of the door panel.

      - Header Capacity: Capable of supporting active breakout leaves up to 220 lb (100 kg) per leaf.

** NOTE TO SPECIFIER ** Select below for single slide or bi-parting ICU/CCU entrances. Delete if not required.

      - Header Size: 8-9/16 inches (218.0 mm) wide by 4-1/2 inches (114 mm) high.

** NOTE TO SPECIFIER ** Select below for single slide telescopic or bi-parting telescopic ICU/CCU entrances. Delete if not required.

      - Header Size: 10-11/16 inches (271 mm) wide by 4-1/2 inches (114 mm) high.

** NOTE TO SPECIFIER ** Choose one of two gasketing options below. Delete "Gasketing" if entrances need to restrict smoke infiltration. Delete "Smoke Gasketing" if entrances do not need to restrict smoke infiltration.

      - Gasketing: Slide-in type, replaceable pile mohair seals.

      - Smoke Gasketing: Slide-in type, replaceable, smoke type gasket capable of withstanding 400 degrees F (204 degrees C) for 30 minutes.

      - Header Access: Continuous hinge at top of header allows cover to swing and allows complete access to operator and internal electronic and mechanical assemblies.

** NOTE TO SPECIFIER ** Entrance needs to be connected to the building ground for the following option - work by others. Delete if not required.

    - Anti-Static Grounding: Fabricate ICU/CCU entrances to be internally grounded to reduce static shock.

** NOTE TO SPECIFIER ** Electrified power transfer is required for privacy glass option. Delete if not required.

    - Electrified Power Transfer: Concealed from header to sliding and sidelite panels. Allows continuous power to sliding panels at all positions during sliding and breakout operations.

      - Rated at 5 amps (600 watts) at 120 VAC maximum.

      - Cable: 18 AWG stranded RoHS compliant UL listed 600 V cable with a temperature range of minus 58 to 194 degrees F (minus 50 to 90 degrees C), with a dynamic bend radius of 6X cable diameter and have a pull tension of 51 lbs. (23 kg) maximum. Withstand 8M cycles at rated dynamic bend radius.

    - Hardware: Provide manufacturer's standard hardware as required for operation indicated.

      - Breakaway Arms and Bottom Pivot Assembly: Allow panels to break out to 90 degrees. Force to breakout sliding panel adjustable to maximum 50 lbf (222 N).

      - Nurse Assist Magnetic Catches: Retain breakout door and sidelite panels in the closed position.

** NOTE TO SPECIFIER ** Delete if not required.

      - Gas Regulated Damper: To control movement of breakout panels.

** NOTE TO SPECIFIER ** Centering wheel is available as an option for smoke rated entrances. Delete if not required.

      - Centering Wheel: To plumb the sliding panel in areas subject to moderate static pressure.

** NOTE TO SPECIFIER ** Latching hardware is standard for smoke rated entrances and optional for non-smoke rated entrances. Delete if not required.

      - Latching Hardware: Provided as indicated.

        - Positive Latch: Mortise type self-latching hookbolt, BHMA A156.5, Grade 1, with lever handles on each side.

          - Levers are installed parallel with the stile and pointing down.

** NOTE TO SPECIFIER ** Select the following if end of lever is required to return to door face by code. Delete if not required.

          - Lever Style: End of lever to have a return towards door face.

          - Electrified strike to automatically release upon activation of sliding door operator.

** NOTE TO SPECIFIER ** The following hardware is required if the entrance is to be connected to an access control system. Delete if not required.

          - The following latching hardware does not replace the positive latching hardware specified above for smoke rated doors.

        - Latching Hardware for Card Reader Activation: Provide latching hardware for connection to an access control system as indicated.

          - Positive Latch: Mortise self-latching hookbolt, BHMA A156.5, Grade 1.

            - No lever handles are to be provided.

          - Electrified strike to automatically release the positive latch upon activation from the access control system and allow the sliding function of the door panels.

          - Electrified strike to be provided with the required power supply and sequencing relays for a complete operable system.

          - Fail Safe Operation: The electrified strike shall unlock the sliding function of the door panels upon loss of power or upon receiving a signal from the smoke detection system and/or fire detection system.

** NOTE TO SPECIFIER ** Automatic releasing/latching is required with the full breakout trackless option. Delete if only the fixed sidelite is required or if full breakout with guide track is required.

        - Automatic Releasing/Latching: Concealed magnetic bolt allows breakout of sidelite panels when sliding panel is in full open position.

** NOTE TO SPECIFIER ** Recessed pull/C-shaped pull is provided standard on sliding ICU/CCU doors, not available with positive latching door hardware. Pulls are not an option for smoke rated entrances. Delete if not required.

      - Door Pulls: Provided as indicated.

        - Active Door Leaves Door Pulls:

          - Breakout Side: Manufacturer's Recessed Door Pull.

          - Non-Breakout Side: 10 inch (254 mm) C-shaped door pull.

            - Door Pull Mounting: Is not to decrease clear opening width.

        - Active Door Leaves Door Pulls:

          - Both Sides: Manufacturer's surface-mounted, 10 inch (254 mm) C-shaped door pull.

            - Door pull mounting shall not decrease clear opening width.

      - Guide Track/Threshold: Manufacturer's threshold as indicated.

** NOTE TO SPECIFIER ** First option below is standard. Second option is available for full breakout entrance. Third option is standard for fixed sidelite models. Fourth option is standard for surface mounted models. Delete options not required.

        - Full Breakout Trackless Design: Floor mounted guide track and threshold not allowed.

          - Breakout from a full open position only.

        - Full Breakout Entrance Guide Track: Floor mounted aluminum guide tracks adjacent to the sidelite portion of the sliding ICU/CCU entrance.

** NOTE TO SPECIFIER ** Select surface or recessed track. Delete option not required.

          - Surface mounted track.

          - Recessed mounted track.

          - Guide track shall allow breakout from any position except when door is latched.

        - Fixed Sidelite Entrance Guide Track: Aluminum guide track integrated in the bottom of the sidelite portion of the sliding ICU/CCU entrance.

          - The guide track is to allow breakout from any position except when door is latched.

** NOTE TO SPECIFIER ** The following is not available for telescopic entrances.

        - Surface Mounted Entrance Guide Track: Aluminum fixed sidelite guide track mounted along the face of the wall. The track shall not extend past the jamb into the door opening.

          - Guide track shall allow breakout from any position except when door is latched.

    - Door Operator and Controller: Electro-mechanical controlled unit utilizing a high-efficiency, energy efficient, DC motor requiring a maximum 3 amp current draw. System to be capable to operate at full performance well beyond brown out and high voltage line conditions (85 to 265 V) sensing changes and adjusting automatically.

      - Adjustable Hold Open Time: 0 to 60 seconds.

      - Power Supply: 120 VAC, 50/60 Hz, 15/20 amp minimum incoming power.

** NOTE TO SPECIFIER ** Convenience battery is optional. Delete if not required.

      - Convenience Battery: Concealed in header. Capable of full operation with blackout conditions, including sensor capabilities for a minimum of 100 cycles.

    - Microprocessor Control Box:

      - Configuration: Factory-adjusted. Pre-set opening and closing speeds.

      - Multi-Position Mode Selector Control: Allow selection of indicated functions to be engaged when switch is turned to the appropriate setting.

** NOTE TO SPECIFIER ** Delete selector not required.

        - Selector: Rotary knob.

        - Selector: Keyed cylinder.

        - Mode Selector Control Mounting: Control to be jamb mounted.

        - Mode Selector Control: Allows the Following Functions:

          - Off.

          - On.

          - Hold Open: Doors activated and held in the full open position.

    - Activation and Safety Control Devices: In accordance with ANSI/BHMA standards, for condition of exposure and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.

      - Coordinate activation and safety devices with door operation and door operator mechanisms.

** NOTE TO SPECIFIER ** Delete the activation and safety devices not required.

      - Activation Device: Knowing Act.

        - Sensor Plate: Touchless, jamb mounted, activation senor plates, black polycarbonate with white letters. Microwave technology has an adjustable range of 2 to 24 inches (51 to 610 mm).

        - Sensor Plate: Touchless, 4-1/2 inch (114 mm) square wall mounted, activation senor plates, black polycarbonate with white letters. Microwave technology has an adjustable range of 2 to 24 inches (51 to 610 mm).

** NOTE TO SPECIFIER ** Retain the following when card reader or keypad activation is required. Delete if not required.

        - Latching hardware is required if the entrance is to be connected to an access control system - See Latching Hardware for Card Reader Activation.

      - Activation Device: Card Readers and/or Keypads.

        - Card readers and keypads provide signal for activation of the opening cycle of the sliding automatic entrance.

        - Provided by others. See Division 28 Section "Electronic Safety and Security".

** NOTE TO SPECIFIER ** Delete Remote VersaMax Management System if not required.

      - Activation Device: Remote. VersaMax Management System: Remote activation system allowing remote activation by patient, nurse, smoke/fire detection system, and/or security system.

      - Safety Presence Sensors:

        - Header Mounted Safety Sensor: ASSA ABLOY OA Presence Safety Sensor.

          - Active infrared reflection technology detects a presence from a single housing mounted on each side of the header.

** NOTE TO SPECIFIER ** The following photoelectric safety beams are provided as a standard feature for the surface mounted entrance.

          - The photoelectric safety beams are provided as an option to the header mounted presence safety sensor for full breakout and fixed sidelite entrances.

        - Photoelectric Safety Beams: Two transmitter/receiver assemblies with infrared photoelectric beams on each side of the frame.

          - Door Movement: Stops when beam is broken.

          - Beams must not be active when doors are fully closed.

        - Breakout Beam: Transmitter/receiver assembly with an infrared photoelectric beam. Stops the sliding door movement when the door is in the breakout position and breaks the photoelectric beam.

          - Presence Detecting Sensors: Field installed and adjusted.

  - ALUMINUM FINISH

    - Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

** NOTE TO SPECIFIER ** Delete finish types and finish options not required.

    - Anodized Finish:

      - AAMA 611, Clear, AA- M12C22A41, Class I, 0.018 mm.

      - AAMA 611, Dark Bronze, AA-M12C22A44, Class I, 0.018 mm.

      - AAMA 611, Color anodized, _____ .

      - AAMA 611, Color anodized, color as indicated on Drawings.

      - AAMA 611, Color anodized, color to be selected by Architect.

    - Painted Finish:

      - Powder coat painted, _____ color.

      - Powder coat painted, color as indicated on Drawings.

      - Powder coat painted, color to be selected by Architect.

      - Kynar finish, 2 coat, _____ color.

      - Kynar finish, 2 coat, color as indicated on Drawings.

      - Kynar finish, 2 coat, color to be selected by Architect.

      - Kynar finish, 3 coat, _____ color.

      - Kynar finish, 3 coat, color as indicated on Drawings.

      - Kynar finish, 3 coat, color to be selected by Architect.

** NOTE TO SPECIFIER ** Delete if not required.

    - MicroShield antimicrobial silver-based ion, baked-on enamel finish on all exposed surfaces including door pulls, door extrusions, rails, and header.

      - Antimicrobial finish must permanently suppress the growth of bacteria, algae, fungus, mold, and mildew by the controlled release of silver ions that attack microbes and inhibit the growth on the treated surfaces.

      - Coating to be EPA registered resulting in a safe and non-toxic finish; chlorinated or synthetic chemical finishes will not be accepted.

- EXECUTION

  - EXAMINATION

    - Do not begin installation until the substrates have been properly constructed and prepared.

    - If substrate preparation is the responsibility of another installer, notify Architect in writing of unsatisfactory preparation before proceeding.

    - Examine doors and frames, with Installer present, for compliance with requirements for installation tolerances, wall and floor construction, and other conditions affecting performance.

    - Examine roughing-in for electrical source power to verify actual locations of wiring connections.

    - Proceed only after such discrepancies or conflicts have been resolved.

  - PREPARATION

    - Clean surfaces thoroughly prior to installation.

    - Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

  - INSTALLATION

    - Install in accordance with manufacturer's instructions, approved submittals and in proper relationship with adjacent construction.

    - Do not install damaged components. Fit frame joints to produce hairline joints free of burrs and distortion. Rigidly secure non-movement joints.

    - Install plumb and true in alignment with established lines and grades without warp or rack of framing members and doors. Anchor securely in place.

      - Install surface mounted hardware using concealed fasteners to the greatest extent possible.

      - Set headers, carrier assemblies, tracks, operating brackets, and guides level and true to location with anchorage for permanent support.

      - Where aluminum will contact dissimilar metals, concrete, or masonry, protect against galvanic action and corrosion.

** NOTE TO SPECIFIER ** Delete if not required.

      - Where smoke control entrances are installed in smoke barriers or partitions, set framing members and header in a bed of sealant to comply with NFPA 105.

** NOTE TO SPECIFIER ** Delete if not required.

    - Magnetic Hold-Open Devices: Connect magnetic hold-open devices to the building fire alarm/sprinkler system as specified in Division 26 and Division 28 Sections.

      - Holding force not to exceed 30lbs for manual door release.

** NOTE TO SPECIFIER ** Delete if not required.

    - Door Operators: Connect door operators to electrical power distribution system as specified in Division 26 Sections.

** NOTE TO SPECIFIER ** Delete if not required.

    - Switchable Privacy Glass: Connect switchable privacy glass to an electrical power distribution system as specified in Division 26 Sections.

    - Glazing: Glaze intensive care unit/critical care unit (ICU/CCU) entrance door panels in accordance with the Glass Association of North America (GANA) Glazing Manual, published recommendations of glass product manufacturer, and published instructions of ICU/CCU entrance manufacturer.

    - Sealants: Comply with requirements specified in division 7 Section "Joint Sealants" to provide a weather tight installation.

      - Set thresholds, bottom guide and track systems and framing members in full bed of sealant.

      - Seal perimeter of framing members with sealant.

** NOTE TO SPECIFIER ** Delete signage option if not required.

    - Signage: Apply signage on both sides of power operated swing doors each door and sidelite as required by ANSI/BHMA A156.19 and manufacturers installation instructions.

    - Signage: Apply signage on both sides of power operated sliding doors and sidelite as required by ANSI/BHMA A156.38 and manufacturers installation instructions.

  - ADJUSTING

    - Adjust alignment of entrances and hardware for smooth, safe operation with minimum air infiltration.

** NOTE TO SPECIFIER ** Delete the following if not required.

    - Adjust door operators and controls for smooth operation and in compliance with ANSI/BHMA A156.19.

    - Adjust door operators and controls for smooth operation and in compliance with ANSI/BHMA A156.38.

    - Verify installation and alignment of all entrance gasketing as required for minimum air infiltration and compliance with specified standards.

  - FIELD QUALITY CONTROL

    - Field Inspection: Coordinate field inspection in accordance with appropriate sections in Division 01.

** NOTE TO SPECIFIER ** Delete door certification option not required.

    - Door Certification: Before placing doors into operation, AAADM certified technician shall inspect and approve doors for compliance with ANSI/BHMA A156.19. Certified technician shall be approved by manufacturer.

    - Door Certification: Before placing doors into operation, AAADM certified technician shall inspect and approve doors for compliance with ANSI/BHMA A156.38. Certified technician shall be approved by manufacturer.

  - CLEANING AND PROTECTION

    - Clean products in accordance with the manufacturer's recommendations.

    - Touch-up, repair or replace damaged products before Substantial Completion.

  - DEMONSTRATION

    - Engage a factory-authorized representative to train Owner's maintenance personnel to adjust, operate, and maintain safe operation of the door.

END OF SECTION