SECTION 08 36 00

COMMERCIAL OVERHEAD SECTIONAL DOORS

Display hidden notes to specifier. (Don't know how? Click Here) 
 Copyright 2008 -  2020 ARCAT, Inc. - All rights reserved

PART 1    GENERAL
1.1	SECTION INCLUDES
A.	Architectural Series:
1.	Glazed aluminum full view sectional overhead doors.
2.	Steel insulated full view sectional overhead doors.
B.	Thermally-Broken and Insulated:
1.	Steel doors with minor ribs, thermally-broken, polyurethane
2.	Flush steel doors with minor ribs, thermally-broken, polyurethane
3.	Raised panel steel doors, thermally-broken polyurethane insulated.
4.	Steel doors with minor ribs, thermally-broken polystyrene insulated.
5.	Flush steel doors with minor ribs, thermally-broken polystyrene insulated.
6.	Raised panel steel doors, thermally-broken polystyrene insulated.
C.	Insulated:
1.	Deep ribbed steel doors, polystyrene insulated.
2.	Flush steel doors, polystyrene insulated.
3.	Raised panel steel doors, polystyrene insulated.
D.	Non-insulated:
1.	Deep ribbed steel doors, non-insulated.
2.	Flush steel doors, non-insulated.
3.	Raised-panel steel doors, non-insulated.
E.	Electric Door Operators.
1.2	RELATED SECTIONS
A.	03300 - Cast-In-Place Concrete.
B.	04200 - Unit Masonry Assemblies.
C.	05500 - Metal Fabrications.
D.	06100 - Rough Carpentry.
E.	07900 - Joint Seals.
F.	08710 - Door Hardware and locks.
G.	09900 - Paints and Coatings.
H.	11150 - Parking Control Equipment: Remote door control.
I.	16050 - Electrical service and connections for powered operators.
1.3	REFERENCES
A.	American Architects Manufacturers Association (AMAA):
1.	AAMA 2604 - Voluntary Specification, Performance Requirements and Test Procedures for Pigmented Organic Coatings on Aluminum Extrusions and Panels.
B.	American National Standards Institute (ANSI):
1.	ANSI/DASMA 102 - American National Standards Specifications for Sectional Doors.
C.	ASTM International (ASTM):
1.	ASTM B 209/209M - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate.
2.	ASTM B 221/221M - Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.
3.	ASTM B 653/653M - Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process.
D.	Door and Access Systems Manufacturers Association (DASMA):
1.	DASMA TDS-163 - R-Value and U-Factor as Applied to A Residential or Commercial Garage Door
1.4	SUBMITTALS
A.	Submit under provisions of Section 01 30 00 - Administrative Requirements.
B.	Product Data: Manufacturer's data sheets on each product to be used, including:
1.	Preparation instructions and recommendations.
2.	Storage and handling requirements and recommendations.
3.	Installation methods.
4.	Operation and maintenance data.
5.	Nameplate data and ratings for motors.
C.	Shop Drawings: Include opening dimensions and required tolerances, connection details, anchorage spacing, hardware locations, and installation details.
D.	Selection Samples: Upon request furnish color samples or 2 x 2 ft (600 x 600 mm) section sample.
1.5	WIND PERFORMANCE REQUIREMENTS
A.	Design doors to withstand positive and negative wind loads as calculated in accordance with applicable building code and detailed in structural documents.
1.6	QUALITY ASSURANCE
A.	Manufacturer Qualifications: Minimum ten years of documented experience.
B.	Installer Qualifications: Minimum five years of documented experience and authorized by the door manufacturer.
1.7	WARRANTY
A.	Manufacturers Limited Warranty aluminum sectional overhead doors. 
1.	Standard finish warranty against cracking, checking, or peeling for 5 years Color Blast Finish option warranty for 5 years; Parts and Hardware for 1 year. Extended 8-Year Hardware Warranty option. 
B.	Manufacturers Limited Warranty steel sectional overhead doors:
1.	Standard finish warranty against cracking, checking, or peeling for 10 years. Custom color option Color Blast Finish limited warranty period for 5 years; Delamination warranty for 10 years; Parts and Hardware for 1 year. Extended 8-Year Hardware Warranty option.
2.	Standard finish warranty against cracking, checking, or peeling for 10 years. Custom color option Color Blast Finish limited warranty period for 5 years. Delamination warranty for 5 years; Parts and Hardware for 1 year. Extended 8-Year Hardware Warranty option.
3.	Standard finish warranty against cracking, checking, or peeling for 10 years. Color Blast Finish option warranty for 5 years; Parts and Hardware for 1 year. Extended 8-Year Hardware Warranty option.
PART 2    PRODUCTS
2.1	MANUFACTURERS
A.	Acceptable Manufacturer: Clopay Corporation, which is located at:<BR />8585 Duke Blvd.<BR />Mason, OH 45040<BR />Toll Free Tel: 800-233-8366<BR />Tel: 513-770-4800<BR />Fax: 888-434-3193<BR />Email: request info (marketing@clopay.com);Web: https://www.clopaydoor.com | https://www.clopaycommercial.com 
B.	Substitutions: Not permitted.
C.	Requests for substitutions will be considered in accordance with provisions of Section 01 60 00 - Product Requirements.
2.2	ARCHITECTURAL SERIES GLAZED ALUMINUM FULL VIEW SECTIONAL OVERHEAD DOORS
A.	Clopay Model 902. Full view heavy duty 2.125 inches (54 mm) door.
1.	Panel Sizes: 44 inches (1118 mm) on center. End panels vary.
B.	Clopay Model 903. Full view heavy duty 2.125 inches (54 mm) Door.
1.	Panel Spacing: Equal panel spacing.
C.	Clopay Model 904. Full view Heavy Duty 2.125 inches (54 mm) Door
1.	Panel Spacing: Equal panel spacing.
D.	Construction: Extruded 6053-T5 aluminum
1.	Aluminum Finish: Factory pre-painted white.
2.	Aluminum Finish: Factory pre-painted brown.
3.	Aluminum Finish: Factory pre-painted simulated bronze anodized.
4.	Aluminum Finish: Clear anodized.
5.	Aluminum Finish: Bronze anodized.
6.	Aluminum Finish: Dark Bronze anodized.
7.	Aluminum Finish: Black anodized.
8.	Aluminum Finish: Custom Color Powder Coat RAL No: ________.
9.	Aluminum Finish: Color Blast. SW Color Code No: ________. SW Color Name: ________.
10.	Panel Section Thickness: 2-1/8 inches (54 mm).
11.	Maximum Door Size (WxH): 24 ft, 2 inches x 18 ft (7.34 x 5.5 m) high.
E.	Windows: 
1.	Glazing Thickness: 1/8 inch (3 mm).
2.	Glazing Thickness: 1/4 inch (6 mm).
3.	Glazing Thickness: 1/2 inch (13 mm) Insulated.
4.	Glazing Thickness: 5/8 inch (16 mm) Polygal.
5.	Glazing Type: Double strength glass.
6.	Glazing Type: Tempered glass.
7.	Glazing Type: Acrylic.
8.	Glazing Type: Triple wall Polygal.
9.	Glazing Type: Low E coated.
10.	Glazing Type: Solid Aluminum panel (color matched)
11.	Glazing Type: Custom ________.
12.	Glazing Finish: Clear.
13.	Glazing Finish: Bronze tint.
14.	Glazing Finish: Grey tint.
15.	Glazing Finish: Frosted/Satin Etch.
16.	Glazing Finish: Custom ________.
F.	Hardware:
1.	Lock Type: One inside slide lock.
2.	Lock Type: Two inside slide locks.
3.	Lock Type: No Lock
4.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
5.	Weatherstripping: Complete perimeter seals.
6.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
7.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
8.	Track configuration to maximize headroom available per plans.
9.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
2.3	ARCHITECTURAL SERIES STEEL INSULATED FULL VIEW SECTIONAL OVERHEAD DOORS
A.	Clopay Model 3729. Premium 2-inch (51 mm) Door: Insulated steel full view doors with minor ribs, thermally-broken, polyurethane insulated.
1.	Maximum Door Size (WxH): 20 ft 2 inches x 18 ft (9.2 x 5.5 m). 
2.	Overall Panel Thickness: 2 inches (51 mm).
3.	Steel Skin Thickness: Interior and Exterior: 27 gauge 0.016 inch (0.40 mm) 
4.	End Stiles: Pre-painted steel. 0.061 inch (1.55 mm) thick. Easy hardware attachment through pre-punched holes.
5.	Astragal: U-shaped flexible PVC in retainer of full-length 0.055 inch (1.4 mm) rigid PVC.
6.	Thermal Resistance (R-value) in accordance with DASMA TDS-163: 18.4 deg F hr sq ft/Btu (3.0 (K sq m)/W).
7.	Insulation: CFC-free and HCFC-free polyurethane, fully encapsulated.
8.	U-Factor: 0.16.
9.	Air infiltration: 0.22 cfm at 25 mph.
10.	Windows: None.
11.	Windows (WxH): 19-1/2 x 16 inches (495 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
12.	Windows (WxH): 42 x 16 inches (1067 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
13.	Finish: Stucco embossed texture. 0.040 inch (1 mm) minor ribs 4 or 5 inches (100 or 125 mm) on center. Interior Color: White.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Almond.
d.	Exterior Color: Sandtone.
e.	Exterior Color: Desert Tan.
f.	Exterior Color: Bronze.
g.	Exterior Color: Gray.
h.	Exterior Color: Glacier White.
i.	Exterior Color: Mocha Brown.
j.	Exterior Color: Black.
k.	Exterior Color: Trinar White.
l.	Exterior Color: Charcoal.
m.	Exterior Color Blast: 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
14.	Lock Type: One inside slide lock.
15.	Lock Type: Two inside slide locks.
16.	Lock Type: Five pin cylinder lock with outside key. 
17.	Lock Type: No Lock
18.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
19.	Weatherstripping: Complete perimeter seals.
20.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
21.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
22.	Track configuration to maximize headroom available per plans.
23.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles.
e.	Maximum cycles in a single shaft line.
B.	Clopay Model 3728. Premium 2-inch (51 mm) flush insulated steel full view doors, thermally-broken, polyurethane insulated.
1.	Maximum Door Size (WxH): 20 ft 2 inches x 18 ft (9.2 x 5.5 m). 
2.	Overall Panel Thickness: 2 inches (51 mm).
3.	Steel Skin Thickness: Interior and Exterior: 27 gauge 0.016 inch (0.40 mm) 
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Pre-painted steel. 0.061 inch (1.55 mm) thick, Easy hardware attachment through pre-punched holes.
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) in accordance with DASMA TDS-163: 18.4 deg F hr sq ft/Btu (3.0 (K sq m)/W).
8.	Insulation: CFC-free and HCFC-free polyurethane, fully encapsulated.
9.	U-Factor: 0.16.
10.	Air infiltration: 0.22 cfm at 25 mph.
11.	Windows: None.
12.	Windows (WxH): 19-1/2 x 16 inches (495 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
13.	Windows (WxH): 42 x 16 inches (1067 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
14.	Finish: Flush Stucco embossed texture. Interior Color: White.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Almond.
d.	Exterior Color: Sandtone.
e.	Exterior Color: Desert Tan.
f.	Exterior Color: Bronze.
g.	Exterior Color: Gray.
h.	Exterior Color: Glacier White.
i.	Exterior Color: Mocha Brown.
j.	Exterior Color: Black.
k.	Exterior Color: Trinar White.
l.	Exterior Color: Charcoal.
m.	Exterior Color Blast: 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
15.	Lock Type: One inside slide lock.
16.	Lock Type: Two inside slide locks.
17.	Lock Type: Five pin cylinder lock with outside key. 
18.	Lock Type: No Lock
19.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
20.	Weatherstripping: Complete perimeter seals.
21.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
22.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
23.	Track configuration to maximize headroom available per plans.
24.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
C.	Clopay Model 3709. Premium 1-3/8-inch (35 mm) Insulated steel full view doors with minor ribs, thermally-broken, polyurethane insulated.
1.	Maximum Door Size (WxH): 18 ft 2 inches x 16 ft (5.5 x 4.9 m).
2.	Overall Panel Thickness: 1-3/8 inches (35 mm).
3.	Steel Skin Thickness: Interior and Exterior: 27 gauge 0.016 inch (0.40 mm) 
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Pre-painted steel. 0.061 inch (1.55 mm) thick, Easy hardware attachment through pre-punched holes.
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) in accordance with DASMA TDS-163: 12.9 deg F hr sq ft/Btu (3.0 (K sq m)/W).
8.	Insulation: CFC-free and HCFC-free polyurethane, fully encapsulated/
9.	U-Factor: 0.19.
10.	Air infiltration: 0.12 cfm at 25 mph/
11.	Windows: None.
12.	Windows (WxH): 19-1/2 x 16 inches (495 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
13.	Windows (WxH): 42 x 16 inches (1067 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
14.	Finish: Stucco embossed texture. 0.040 inch (1 mm) minor ribs 4 or 5 inches (100 or 125 mm) on center. Interior Color: White.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Almond.
d.	Exterior Color: Sandtone.
e.	Exterior Color: Desert Tan.
f.	Exterior Color: Bronze.
g.	Exterior Color: Gray.
h.	Exterior Color: Glacier White.
i.	Exterior Color: Mocha Brown.
j.	Exterior Color: Black.
k.	Exterior Color: Trinar White.
l.	Exterior Color: Charcoal.
m.	Exterior Color Blast: 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
15.	Lock Type: One inside slide lock.
16.	Lock Type: Two inside slide locks.
17.	Lock Type: Five pin cylinder lock with outside key. 
18.	Lock Type: No Lock
19.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
20.	Weatherstripping: Complete perimeter seals.
21.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
22.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
23.	Track configuration to maximize headroom available per plans.
24.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles.
e.	Maximum cycles in a single shaft line.
D.	Clopay Model 3708. Premium 1-3/8-inch (35 mm) Flush insulated steel full view doors, thermally-broken, polyurethane insulated.
1.	Maximum Door Size (WxH): 18 ft 2 inches x 16 ft (5.5 x 4.9 m).
2.	Overall Panel Thickness: 1-3/8 inches (35 mm).
3.	Steel Skin Thickness: Interior and Exterior: 27 gauge 0.016 inch (0.40 mm) 
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Pre-painted steel. 0.061 inch (1.55 mm) thick, Easy hardware attachment through pre-punched holes.
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) in accordance with DASMA TDS-163: 12.9 deg F hr sq ft/Btu (3.0 (K sq m)/W).
8.	Insulation: CFC-free and HCFC-free polyurethane, fully encapsulated/
9.	U-Factor: 0.19.
10.	Air infiltration: 0.12 cfm at 25 mph.
11.	Windows: None.
12.	Windows (WxH): 19-1/2 x 16 inches (495 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
13.	Windows (WxH): 42 x 16 inches (1067 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
14.	Finish: Flush stucco embossed texture. Interior Color: White.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Almond.
d.	Exterior Color: Sandtone.
e.	Exterior Color: Desert Tan.
f.	Exterior Color: Bronze.
g.	Exterior Color: Gray.
h.	Exterior Color: Glacier White.
i.	Exterior Color: Mocha Brown.
j.	Exterior Color: Black.
k.	Exterior Color: Trinar White.
l.	Exterior Color: Charcoal.
m.	Exterior Color Blast:
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
15.	Lock Type: One inside slide lock.
16.	Lock Type: Two inside slide locks.
17.	Lock Type: Five pin cylinder lock with outside key. 
18.	Lock Type: No Lock
19.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
20.	Weatherstripping: Complete perimeter seals.
21.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
22.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
23.	Track configuration to maximize headroom available per plans.
24.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
E.	Clopay Model 3209. Premium 2-inch (51 mm) Insulated steel full view doors with minor ribs, thermally-broken, polystyrene insulated.
1.	Maximum Door Size (WxH): 20 ft 2 inches x 18 ft (9.2 x 5.5 m). 
2.	Overall Panel Thickness: 2 inches (51 mm).
3.	Steel Skin Thickness: Exterior: 24 gauge 0.022 inch (0.56 mm). Interior: 27 gauge 0.016 inch (0.40 mm) interior.
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Pre-painted steel. 0.061 inch (1.55 mm) thick, Easy hardware attachment through pre-punched holes.
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) in accordance with DASMA TDS-163: 9.1 deg F hr sq ft/Btu (3.0 (K sq m)/W).
8.	U-Factor: 0.23.
9.	Air infiltration: 0.34 cfm at 25 mph.
10.	Windows: None.
11.	Windows (WxH): 19-1/2 x 16 inches (495 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
12.	Windows (WxH): 42 x 16 inches (1067 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
13.	Finish: Stucco embossed texture. 0.040 inch (1 mm) minor ribs 4 or 5 inches (100 or 125 mm) on center. Interior Color: White.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Gray
d.	Exterior Color: Black
e.	Exterior Color Blast: 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
14.	Lock Type: One inside slide lock.
15.	Lock Type: Two inside slide locks.
16.	Lock Type: Five pin cylinder lock with outside key. 
17.	Lock Type: No Lock
18.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
19.	Weatherstripping: Complete perimeter seals.
20.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
21.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
22.	Track configuration to maximize headroom available per plans.
23.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
F.	Clopay Model 3208. Premium 2-inch (51 mm) Flush insulated steel full view doors, thermally-broken, polystyrene insulated.
1.	Maximum Door Size (WxH): 20 ft 2 inches x 18 ft (9.2 x 5.5 m) high. 
2.	Overall Panel Thickness: 2 inches (51 mm).
3.	Steel Skin Thickness: Exterior: 24 gauge 0.022 inch (0.56 mm). Interior: 27 gauge 0.016 inch (0.40 mm) interior.
4.	End Stiles: Pre-painted Steel. 0.061 inch (1.55 mm) thick. Easy hardware attachment through pre-punched holes.
5.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 9.1 deg F hr sq ft/Btu (1.6 (K sq m)/W).
8.	U-Factor: 0.23.
9.	Air infiltration: 0.34 cfm at 25 mph.
10.	Windows: None.
11.	Windows (WxH): 19-1/2 x 16 inches (495 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
12.	Windows (WxH): 42 x 16 inches (1067 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
13.	Finish: Flush stucco embossed texture. Interior Color: White.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Gray.
d.	Exterior Color: Black
e.	Exterior Color Blast: 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
14.	Lock Type: One inside slide lock.
15.	Lock Type: Two inside slide locks.
16.	Lock Type: Five pin cylinder lock with outside key. 
17.	Lock Type: No Lock
18.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
19.	Weatherstripping: Complete perimeter seals.
20.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
21.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
22.	Track configuration to maximize headroom available per plans.
23.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
G.	Clopay Model 3159. Premium 1-3/8-inch (35 mm) Insulated steel full view doors with minor ribs, thermally-broken, polystyrene insulated.
1.	Maximum Door Size (WxH): 18 ft 2 inches x 16 ft, (5.5 x 4.9 m). 
2.	Overall Panel Thickness: 1-3/8 inches (35 mm).
3.	Steel Skin Thickness: Exterior and Interior: 27 gauge, 0.016 inch (0.40 mm) 
4.	End Stiles: Pre-painted steel. 0.061 inch (1.55 mm) thick, Easy hardware attachment through pre-punched holes.
5.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 6.5 deg F hr sq ft/Btu (1.15 (K sq m)/W).
8.	U-Factor: 0.27.
9.	Air infiltration: 0.41 cfm at 25 mph.
10.	Windows: None.
11.	Windows (WxH): 19-1/2 x 16 inches (495 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
12.	Windows (WxH): 42 x 16 inches (1067 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
13.	Finish: Stucco embossed texture. 0.040 inch (1 mm) minor ribs 4 or 5 inches (100 or 125 mm) on center. Interior Color: White.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Almond.
d.	Exterior Color: Sandtone.
e.	Exterior Color: Desert Tan.
f.	Exterior Color: Bronze.
g.	Exterior Color: Gray.
h.	Exterior Color: Glacier White.
i.	Exterior Color: Mocha Brown.
j.	Exterior Color: Black.
k.	Exterior Color: Trinar White.
l.	Exterior Color: Charcoal.
m.	Exterior Color Blast: 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
14.	Lock Type: One inside slide lock.
15.	Lock Type: Two inside slide locks.
16.	Lock Type: Five pin cylinder lock with outside key. 
17.	Lock Type: No Lock
18.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
19.	Weatherstripping: Complete perimeter seals.
20.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
21.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
22.	Track configuration to maximize headroom available per plans.
23.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
H.	Clopay Model 3158. Premium 1-3/8-inch (35 mm) Flush insulated steel full view doors, thermally-broken, polystyrene insulated.
1.	Maximum Door Size (WxH): 18 ft 2 inches x 156 ft (5.5 x 4.9 m) high. 
2.	Overall Panel Thickness: 1-3/8 inches (35 mm).
3.	Steel Skin Thickness: Exterior and Interior: 27 gauge, 0.016 inch (0.40 mm) 
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Pre-painted steel. 0.061 inch (1.55 mm) thick, Easy hardware attachment through pre-punched holes.
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 6.5 deg F hr sq ft/Btu (1.15 (K sq m)/W). 
8.	U-Factor: 0.27.
9.	Air infiltration: 0.41 cfm at 25 mph.
10.	Windows: None.
11.	Windows (WxH): 19-1/2 x 16 inches (495 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
12.	Windows (WxH): 42 x 16 inches (1067 x 406 mm). Extruded polypropylene.
a.	Glazing: 1/8 inch (3 mm) tempered.
b.	Glazing: 1/8 inch (3 mm) frosted tempered.
c.	Glazing: 3/4 inch (19 mm) insulated tempered.
d.	Glazing: 3/4 inch (19 mm) insulated frosted tempered.
13.	Finish: Flush stucco embossed texture Interior Color: White.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Almond.
d.	Exterior Color: Sandtone.
e.	Exterior Color: Desert Tan.
f.	Exterior Color: Bronze.
g.	Exterior Color: Gray.
h.	Exterior Color: Glacier White.
i.	Exterior Color: Mocha Brown.
j.	Exterior Color: Black.
k.	Exterior Color: Trinar White.
l.	Exterior Color: Charcoal.
m.	Exterior Color Blast: 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
14.	Lock Type: One inside slide lock.
15.	Lock Type: Two inside slide locks.
16.	Lock Type: Five pin cylinder lock with outside key. 
17.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
18.	Weatherstripping: Complete perimeter seals.
19.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
20.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
21.	Track configuration to maximize headroom available per plans.
22.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
2.4	STEEL DOORS WITH MINOR RIBS, THERMALLY-BROKEN, POLYURETHANE 
A.	Clopay Model 3730. Premium 3-inch (75 mm) Style: Steel doors with minor ribs, thermally-broken, polyurethane insulated.
1.	Maximum Door Size (WxH): 30 ft 2 inches x 18 ft (9.2 x 5.5 m) high.
2.	Overall Panel Thickness: 3 inches (75 mm).
3.	Steel Skin Thickness: Exterior and Interior: 27 gauge, 0.016 inch (0.40 mm) 
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Pre-painted steel. 0.061 inch (1.55 mm) thick, Easy hardware attachment through pre-punched holes.
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 22.2 deg F hr sq ft/Btu (4.40 (K sq m)/W).
8.	Insulation: CFC-free and HCFC-free polyurethane, fully encapsulated.
9.	U-Factor: 0.15.
10.	Air Infiltration: 0.20 cfm at 25 mph.
11.	Windows: None.
12.	PVC Windows (WxH): 8 x 24 inches (200 x 600 mm).
a.	Glazing: 2 inch (51 mm) insulated triple pane DSB glass. 
13.	PVC Windows (WxH): 12 x 24 inches (305 x 600 mm).
a.	Glazing: 2 inch (51 mm) insulated triple pane DSB glass.
14.	Finish: Stucco embossed texture. 0.040 inch (1 mm) minor ribs 4 or 5 inches (100 or 125 mm) on center. Interior Color: White.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color Blast: 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
15.	Lock Type: One inside slide lock.
16.	Lock Type: Two inside slide locks.
17.	Lock Type: Five pin cylinder lock with outside key. 
18.	Lock Type: No Lock
19.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
20.	Weatherstripping: Complete perimeter seals.
21.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
22.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
23.	Track configuration to maximize headroom available per plans.
24.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
B.	Clopay Model 3720. Premium Duty 2-inches (51 mm) steel doors with minor ribs, thermally-broken, polyurethane insulated.
1.	Maximum Door Size (WxH): 32 ft, 2 inches x 26 ft (9.8 x 7.9 m).
2.	Overall Panel Thickness: 2-inches (51 mm).
3.	Steel Skin Thickness: Exterior and Interior: 27 gauge, 0.016 inch (0.40 mm) 
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Galvanized steel. Easy hardware attachment through pre-punched holes. Single End Hinge Style: 18 gauge, 0.045 inch (1.14 mm) thick. Double End Hinge Style: 16 gauge 0.056 inch (1.42 mm).
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 18.4 deg F hr sq ft/Btu (3.0 (K sq m)/W).
8.	Insulation: CFC-free and HCFC-free polyurethane, fully encapsulated.
9.	U-Factor: 0.16.
10.	Air Infiltration: .022 cfm at 25 mph.
11.	Windows: None.
12.	Windows (WxH): 8 x 24 inches (200 x 600 mm). Extruded polypropylene 
a.	Glazing: 1 inch (25 mm) insulated glass.
b.	Glazing: 1 inch (25 mm) insulated tempered glass.
c.	Glazing: 1/4 inch (6 mm) impact resistant Lexan.
13.	Windows (WxH): 12 x 24 inches (305 x 600 mm). Extruded polypropylene.
a.	Glazing: 1 inch (25 mm) insulated glass.
b.	Glazing: 1 inch (25 mm) insulated tempered glass.
c.	Glazing: 1/4 inch (6 mm) impact resistant Lexan.
14.	Windows: Full vision aluminum section, pre-painted to match door finish.
a.	Glazing: 1/8 inch (3 mm) DSB glass
b.	Glazing: 1/4 inch (6 mm) tempered glass
c.	Glazing: 1/2 inch (13 mm) insulated glass
d.	Glazing: Custom ________.
15.	Windows WxH): 13 x 26 inches (303 x 606 mm). Black extruded polypropylene with rounded corners.
a.	Glazing: 5/8 inch (16 mm) double pane acrylic.
b.	Glazing: 5/8 inch (16 mm) double pane lexan.
16.	Finish: Interior stucco embossed texture with shallow U ribbed pattern. Interior Color: White. Exterior stucco embossed with ribbed pattern, 
a.	Exterior Color: White.
b.	Exterior Color: Glacier White.
c.	Exterior Color: Brown.
d.	Exterior Color: Commercial Tan.
e.	Exterior Color: Mocha Brown.
f.	Exterior Color: Charcoal.
g.	Exterior Color: Commercial Gray.
h.	Exterior Color: Trinar White.
i.	Exterior Color: Trinar Beige.
j.	Exterior Color Blast.
1)	SW Color Code No: _______.
2)	SW Color Name: ________.
17.	Lock Type: One inside slide lock.
18.	Lock Type: Two inside slide locks.
19.	Lock Type: Five pin cylinder lock with outside key. 
20.	Lock Type: No Lock.
21.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
22.	Weatherstripping: Complete perimeter seals. Flexible top and jamb seals U shaped bottom seal.
23.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
24.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
25.	Track configuration to maximize headroom available per plans.
26.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
27.	Break-Away Bottom Section: Integral part of door. Fiberglass or 1/8 inch (3 mm) polycarbonate lined bottom section with flexible neoprene rubber side edges. Exterior to match door face. 
a.	Single Breakaway Bottom Section: For doors up to 20 ft (6 m) wide. 
b.	Double Breakaway Bottom Section: For doors up to 14 ft (4.3 m) wide. 
28.	Pass Door (Walk-Through Service Door): 32 x 80 inches (813 x 2032 mm) with aluminum frame, geared hinge, and pneumatic door closer; exterior matching door face; integral shiplap weather seal; keyed dead latch security lock.
C.	Clopay Model 3724. Premium duty 2 inches (51 mm) steel doors with minor ribs, thermally-broken, polyurethane insulated.
1.	Maximum Door Size (WxH): 32 ft 2 inches x 26 ft (9.8 x 7.9 m). 
2.	Overall Panel Thickness: 2-inches (51 mm).
3.	Steel Skin Thickness: Exterior: 24 gauge 0.022 inch (0.56 mm). Interior: 27 gauge 0.016 inch (0.40 mm) interior.
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Galvanized steel. Easy hardware attachment through pre-punched holes. Single End Hinge Style: 18 gauge, 0.045 inch (1.14 mm) thick. Double End Hinge Style: 16 gauge 0.056 inch (1.42 mm).
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 18.4 deg F hr sq ft/Btu (3.0 (K sq m)/W).
8.	Insulation: CFC-free and HCFC-free polyurethane. Fully encapsulated.
9.	U-Factor: 0.16.
10.	Air Infiltration: .022 cfm at 25 mph.
11.	Windows: None.
12.	Windows (WxH): 8 x 24 inches (200 x 600 mm). Extruded polypropylene 
a.	Glazing: 1 inch (25 mm) insulated glass.
b.	Glazing: 1 inch (25 mm) insulated tempered glass.
c.	Glazing: 1/4 inch (6 mm) impact resistant Lexan.
13.	Windows (WxH): 12 x 24 inches (305 x 600 mm). Extruded polypropylene.
a.	Glazing: 1 inch (25 mm) insulated glass.
b.	Glazing: 1 inch (25 mm) insulated tempered glass.
c.	Glazing: 1/4 inch (6 mm) impact resistant Lexan.
14.	Windows: Full vision aluminum section, pre-painted to match door finish.
a.	Glazing: 1/8 inch (3 mm) DSB glass
b.	Glazing: 1/4 inch (6 mm) tempered glass
c.	Glazing: 1/2 inch (13 mm) insulated glass
d.	Glazing: Custom ________.
15.	Windows WxH): 13 x 26 inches (303 x 606 mm). Black extruded polypropylene with rounded corners.
a.	Glazing: 5/8 inch (16 mm) double pane acrylic.
b.	Glazing: 5/8 inch (16 mm) double pane lexan.
16.	Finish: Interior stucco embossed texture with shallow U ribbed pattern. Interior Color: White. Exterior stucco embossed with ribbed pattern. 
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Commercial Tan.
d.	Exterior Color: Gray.
e.	Exterior Color: Black.
f.	Exterior Color: Trinar White
g.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
17.	Lock Type: One inside slide lock.
18.	Lock Type: Two inside slide locks.
19.	Lock Type: Five pin cylinder lock with outside key. 
20.	Lock Type: No Lock
21.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
22.	Weatherstripping: Complete perimeter seals.
23.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
24.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
25.	Track configuration to maximize headroom available per plans.
26.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
27.	Break-Away Bottom Section: Integral part of door. Fiberglass with flexible neoprene rubber side edges. Exterior to match door face. 
a.	Single Breakaway Bottom Section: For doors up to 20 ft (6 m) wide. 
b.	Double Breakaway Bottom Section: For doors up to 14 ft (4.3 m) wide. 
28.	Pass Door (Walk-Through Service Door): 32 x 80 inches (813 x 2032 mm) with aluminum frame, geared hinge, and pneumatic door closer; exterior matching door face; integral shiplap weather seal; keyed dead latch security lock.
D.	Clopay Model 3717. Heavy duty 1-3/4-inches (45 mm) steel doors with minor ribs, thermally-broken, polyurethane insulated.
1.	Maximum Door Size (WxH): 32 ft, 2 inches x 26 ft (9.8 x 7.9 m).
2.	Overall Panel Thickness: 1-3/4 inches (45 mm).
3.	Steel Skin Thickness: Exterior and Interior: 27 gauge, 0.016 inch (0.40 mm) 
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Galvanized steel. Easy hardware attachment through pre-punched holes. Single End Hinge Style: 18 gauge, 0.045 inch (1.14 mm) thick. Double End Hinge Style: 16 gauge 0.056 inch (1.42 mm).
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value): 16.2 deg F hr sq ft/Btu (2.7 (K sq m)/W); calculated door section R-value in accordance with DASMA TDS-163.
8.	Insulation: CFC-free and HCFC-free polyurethane, fully encapsulated.
9.	U-Factor: 18.
10.	Air Infiltration: .25 cfm at 25 mph.
11.	Windows: None.
12.	Windows (WxH): 8 x 24 inches (200 x 600 mm). Extruded polypropylene 
a.	Glazing: 7/8 inch (22 mm) insulated glass.
b.	Glazing: 7/8 inch (22 mm) insulated tempered glass.
c.	Glazing: 1/4 inch (6 mm) impact resistant Lexan.
13.	Windows (WxH): 12 x 24 inches (305 x 600 mm). Extruded polypropylene.
a.	Glazing: 7/8 inch (22 mm) insulated glass.
b.	Glazing: 7/8 inch (22 mm) insulated tempered glass.
c.	Glazing: 1/4 inch (6 mm) impact resistant Lexan.
14.	Windows: Full vision aluminum section, pre-painted to match door finish.
a.	Glazing: 1/8 inch (3 mm) DSB glass
b.	Glazing: 1/4 inch (6 mm) tempered glass
c.	Glazing: 1/2 inch (13 mm) insulated glass
d.	Glazing: Custom ________.
15.	Windows WxH): 13 x 26 inches (303 x 606 mm). Black extruded polypropylene with rounded corners.
a.	Glazing: 5/8 inch (16 mm) double pane acrylic.
b.	Glazing: 5/8 inch (16 mm) double pane lexan.
16.	Finish: Interior stucco embossed texture with shallow U ribbed pattern. Interior Color: White. Exterior stucco embossed with ribbed pattern.
a.	Exterior Color: White.
b.	Exterior Color: Glacier White
c.	Exterior Color: Brown.
d.	Exterior Color: Mocha Brown
e.	Exterior Color: Charcoal
f.	Exterior Color: Commercial Tan.
g.	Exterior Color: Gray.
h.	Exterior Color: Trinar White.
i.	Exterior Color: Trinar Beige.
j.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
17.	Lock Type: One inside slide lock.
18.	Lock Type: Two inside slide locks.
19.	Lock Type: Five pin cylinder lock with outside key. 
20.	Lock Type: No Lock
21.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
22.	Weatherstripping: Complete perimeter seals.
23.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
24.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
25.	Track configuration to maximize headroom available per plans.
26.	Torsion Spring Counterbalance: Mechanism sized to weight of door. Helically wound, oil tempered spring on steel shaft. Cable drum of die cast aluminum with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
27.	Break-Away Bottom Section: Integral part of door. Fiberglass with flexible neoprene rubber side edges. Exterior to match door face. 
a.	Single Breakaway Bottom Section: For doors up to 20 ft (6 m) wide. 
b.	Double Breakaway Bottom Section: For doors up to 14 ft (4.3 m) wide. 
E.	Clopay Model 3715. Standard duty 1-3/8-inches (35 mm) steel doors with minor ribs, thermally-broken, polyurethane insulated.
1.	Maximum Door Size (WxH): 20 ft, 6 inches x 16 ft (6.2 x 4.9 m) high. 
2.	Overall Panel Thickness: 1-3/8-inches (35 mm).
3.	Steel Skin Thickness: Exterior and Interior: 27 gauge, 0.016 inch (0.40 mm) 
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Galvanized steel. 20 gauge, 0.034 inch (.86 mm) thick. Easy hardware attachment through pre-punched holes.
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value): 12.9 deg F hr sq ft/Btu (2.3 (K sq m)/W); calculated door section R-value in accordance with DASMA TDS-163.
8.	Insulation: CFC-free and HCFC-free polyurethane, fully encapsulated.
9.	U-Factor: 0.19.
10.	Air Infiltration: 0.12 cfm at 25 mph.
11.	Windows: None.
12.	Windows (WxH): 8 x 24 inches (200 x 600 mm). Extruded polypropylene 
a.	Glazing: 1/2 inch (12 mm) insulated glass.
b.	Glazing: 1/2 inch (12 mm) insulated tempered glass.
13.	Windows (WxH): 12 x 24 inches (305 x 600 mm). Extruded polypropylene.
a.	Glazing: 1/2 inch (12 mm) insulated glass.
b.	Glazing: 1/2 inch (12 mm) insulated tempered glass.
14.	Windows: Full vision aluminum section, pre-painted to match door finish.
a.	Glazing: 1/8 inch (3 mm) DSB glass
b.	Glazing: 1/4 inch (6 mm) tempered glass
c.	Glazing: 1/2 inch (13 mm) insulated glass
d.	Glazing: Custom ________.
15.	Finish: Interior stucco embossed texture with ribbed pattern. Interior Color: White. Exterior stucco embossed with ribbed pattern.
a.	Exterior Color: White.
b.	Exterior Color: Glacier White
c.	Exterior Color: Brown.
d.	Exterior Color: Mocha Brown
e.	Exterior Color: Charcoal
f.	Exterior Color: Commercial Tan.
g.	Exterior Color: Gray.
h.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
16.	Lock Type: One inside slide lock.
17.	Lock Type: Two inside slide locks.
18.	Lock Type: Five pin cylinder lock with outside key. 
19.	Lock Type: No Lock.
20.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
21.	Weatherstripping: Complete perimeter seals.
22.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
23.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
24.	Track configuration to maximize headroom available per plans.
25.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles.
e.	Maximum cycles in a single shaft line.
2.5	FLUSH STEEL DOORS, THERMALLY-BROKEN, POLYURETHANE INSULATED
A.	Clopay Model 3721. Premium Duty Insulated 2 inches (51 mm) Flush steel doors, thermally-broken, polyurethane insulated.
1.	Maximum Door Size (WxH): 24 ft, 2 inches x 18 ft (7.4 m x 5.5 m).
2.	Overall Panel Thickness: 2 inches (51 mm).
3.	Steel Skin Thickness: Exterior and Interior: 27 gauge, 0.016 inch (0.40 mm) 
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Galvanized steel. Easy hardware attachment through pre-punched holes. Single End Hinge Style: 18 gauge, 0.045 inch (1.14 mm) thick. Double End Hinge Style: 16 gauge 0.056 inch (1.42 mm).
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 18.4 deg F hr sq ft/Btu (2.7 (K sq m)/W).
8.	U-Factor: 0.16.
9.	Air Infiltration: 0.022 cfm at 25 mph
10.	Finish: Interior: Stucco embossed texture with shallow U ribbed pattern. Interior Color: White. Exterior: Woodgrain embossed texture with flush exterior panel.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Almond.
d.	Exterior Color: Desert Tan.
e.	Exterior Color: Sandtone.
f.	Exterior Color: Commercial Tan
g.	Exterior Color: Charcoal
h.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
11.	Windows: None. 
12.	Windows (WxH): 12 x 19.5 inches (305 x 495 mm). Extruded polypropylene 
a.	Glazing: 1/8 inch (3 mm) DSB sheet glass. 
b.	Glazing: 1/8 inch (3 mm) acrylic sheet. 
c.	Glazing: 1/2 inch (12 mm) insulated glass glazing 
13.	Windows (WxH): 12 x 40.5 inches (305 x 1029 mm). Extruded polypropylene 
a.	Glazing: 1/8 inch (3 mm) DSB sheet glass. 
b.	Glazing: 1/8 inch (3 mm) acrylic sheet. 
c.	Glazing: 1/2 inch (12 mm) insulated glass glazing
14.	Lock Type: One inside slide lock.
15.	Lock Type: Two inside slide locks.
16.	Lock Type: Five pin cylinder lock with outside key. 
17.	Lock Type: No Lock
18.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
19.	Weatherstripping: Complete perimeter seals. Flexible top and jamb seals. U shaped bottom seal.
20.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
21.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
22.	Track configuration to maximize headroom available per plans.
23.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
B.	Clopay Model 3722. Premium duty insulated 2-inches (51 mm) Flush steel doors, thermally-broken, polyurethane insulated.
1.	Maximum Door Size (WxH): 32 ft, 2 inches x 24 ft (9.8 x 7.3 m). 
2.	Overall Panel Thickness: 2 inches (51 mm).
3.	Steel Skin Thickness: Exterior: 20 ga .034 inch (0.86 mm). Interior: 27 gauge 0.016 inch (0.40 mm).
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Galvanized steel. Easy hardware attachment through pre-punched holes. Single End Hinge Style: 18 gauge, 0.045 inch (1.14 mm) thick. Double End Hinge Style: 16 gauge 0.056 inch (1.42 mm).
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 18.4 deg F hr sq ft/Btu (2.7 (K sq m)/W).
8.	Insulation: CFC-free and HCFC-free polyurethane, fully encapsulated.
9.	U-Factor: 0.16.
10.	Air Infiltration: 0.22 cfm at 25 mph.
11.	Finish: Interior stucco embossed texture with shallow U ribbed pattern. Color: White. Exterior: Stucco embossed texture with flush exterior panel. Color as follows:
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
12.	Windows: None.
13.	Windows (WxH): 8 x 24 inches (200 x 600 mm). Extruded polypropylene 
a.	Glazing: 7/8 inch (22 mm) insulated glass.
b.	Glazing: 7/8 inch (22 mm) insulated tempered glass.
14.	Windows (WxH): 12 x 24 inches (305 x 600 mm). Extruded polypropylene.
a.	Glazing: 7/8 inch (22 mm) insulated glass.
b.	Glazing: 7/8 inch (22 mm) insulated tempered glass.
15.	Windows: Full vision aluminum section, pre-painted to match door finish.
a.	Glazing: 1/8 inch (3 mm) DSB glass
b.	Glazing: 1/4 inch (6 mm) tempered glass
c.	Glazing: 1/2 inch (13 mm) insulated glass
d.	Glazing: Custom ________.
16.	Windows WxH): 13 x 26 inches (303 x 606 mm). Black extruded polypropylene with rounded corners.
a.	Glazing: 5/8 inch (16 mm) double pane acrylic.
b.	Glazing: 5/8 inch (16 mm) double pane lexan.
17.	Lock Type: One inside slide lock.
18.	Lock Type: Two inside slide locks.
19.	Lock Type: Five pin cylinder lock with outside key. 
20.	Lock Type: No Lock
21.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
22.	Weatherstripping: Complete perimeter seals. 
23.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
24.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
25.	Track configuration to maximize headroom available per plans.
26.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
27.	Break-Away Bottom Section: Integral part of door. Fiberglass with flexible neoprene rubber side edges. Exterior to match door face
a.	Single Breakaway Bottom Section: For doors up to 20 ft (6 m) wide
b.	Double Breakaway Bottom Section: For doors up to 14 ft (4.3 m) wide
28.	Pass Door (Walk-Through Service Door): 32 x 80 inches (813 x 2032 mm) with aluminum frame, geared hinge, and pneumatic door closer; exterior matching door face; integral shiplap weather seal; keyed dead latch security lock
C.	Clopay Model 3718. Heavy duty 1-3/4-inches (45 mm) flush steel doors, thermally-broken, polyurethane insulated.
1.	Maximum Door Size (WxH): 32 ft, 2 inches x 24 ft (9.8 x 7.3 m).
2.	Overall Panel Thickness: 1-3/4-inches (45 mm).
3.	Steel Skin Thickness: Exterior and Interior: 27 gauge, 0.016 inch (0.40 mm) 
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Galvanized steel. Easy hardware attachment through pre-punched holes. Single End Hinge Style: 18 gauge, 0.045 inch (1.14 mm) thick. Double End Hinge Style: 16 gauge 0.056 inch (1.42 mm).
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 16.2 deg F hr sq ft/Btu (2.7 (K sq m)/W).
8.	Insulation: CFC-free and HCFC-free polyurethane, fully encapsulated.
9.	U-Factor: 0.18.
10.	Air Infiltration: 0.25 cfm at 25 mph.
11.	Finish: Interior stucco embossed texture with shallow U ribbed pattern. Interior Color: White. Exterior stucco embossed texture with flush panel. 
a.	Exterior Color: White.
b.	Exterior Color: Glacier White
c.	Exterior Color: Brown.
d.	Exterior Color: Mocha Brown.
e.	Exterior Color: Charcoal. 
f.	Exterior Color: Commercial Tan.
g.	Exterior Color: Gray. 
h.	Exterior Color: Trinar White. 
i.	Exterior Color: Trinar Beige.
j.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
12.	Windows: None.
13.	Windows (WxH): 8 x 24 inches (200 x 600 mm). Extruded polypropylene 
a.	Glazing: 7/8 inch (22 mm) insulated glass.
b.	Glazing: 7/8 inch (22 mm) insulated tempered glass.
c.	Glazing: 1/4 inch (6 mm) impact resistant Lexan.
14.	Windows (WxH): 12 x 24 inches (305 x 600 mm). Extruded polypropylene.
a.	Glazing: 7/8 inch (22 mm) insulated glass.
b.	Glazing: 7/8 inch (22 mm) insulated tempered glass.
c.	Glazing: 1/4 inch (6 mm) impact resistant Lexan.
15.	Windows: Full vision aluminum section, pre-painted to match door finish.
a.	Glazing: 1/8 inch (3 mm) DSB glass.
b.	Glazing: 1/4 inch (6 mm) tempered glass.
c.	Glazing: 1/2 inch (13 mm) insulated glass.
d.	Glazing: Custom ________.
16.	Windows WxH): 13 x 26 inches (303 x 606 mm). Black extruded polypropylene with rounded corners.
a.	Glazing: 5/8 inch (16 mm) double pane acrylic.
b.	Glazing: 5/8 inch (16 mm) double pane lexan.
17.	Lock Type: One inside slide lock.
18.	Lock Type: Two inside slide locks.
19.	Lock Type: Five pin cylinder lock with outside key. 
20.	Lock Type: No Lock.
21.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
22.	Weatherstripping: Complete perimeter seals.
23.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
24.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
25.	Track configuration to maximize headroom available per plans.
26.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles.
e.	Maximum cycles in a single shaft line.
27.	Break-Away Bottom Section: Integral part of door. Fiberglass with flexible neoprene rubber side edges. Exterior to match door face.
a.	Single Breakaway Bottom Section: For doors up to 20 ft (6 m) wide.
b.	Double Breakaway Bottom Section: For doors up to 14 ft (4.3 m) wide.
2.6	RAISED PANEL STEEL DOORS, THERMALLY-BROKEN, POLYURETHANE INSULATED
A.	Clopay Model 3723. Premium duty insulated 2-inch (51 mm) raised panel steel doors, thermally-broken, polyurethane insulated.
1.	Maximum Door Size (WxH): 24 ft, 2 inches x 18 ft (7.4 x 5.5 m).
2.	Steel Skin Thickness, Exterior and Interior: 27 gauge, 0.016 inch (0.40 mm).
3.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
4.	Finish: Interior stucco embossed texture with shallow U ribbed pattern. Interior Color: White. Exterior: Stucco embossed texture with raised exterior panel.
a.	Exterior Color: White.
b.	Exterior Color: Glacier White.
c.	Exterior Color: Almond.
d.	Exterior Color: Sandtone.
e.	Exterior Color: Desert Tan.
f.	Exterior Color: Commercial Tan.
g.	Exterior Color: Brown.
h.	Exterior Color: Charcoal.
i.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
5.	Overall Panel Thickness: 2-inches (51 mm).
6.	End Stiles: Galvanized steel. Easy hardware attachment through pre-punched holes. Single End Hinge Style: 18 gauge, 0.045 inch (1.14 mm) thick. Double End Hinge Style: 16 gauge 0.056 inch (1.42 mm).
7.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
8.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 18.4 deg F hr sq ft/Btu (3.0 (K sq m)/W).
9.	Insulation: CFC-free and HCFC-free polyurethane, fully encapsulated.
10.	U-Factor: 0.16.
11.	Air Infiltration: 0.22 cfm at 25 mph.
12.	Windows: None.
13.	PVC Windows (WxH): 12 x 19.5 inches (305 x 495 mm)
a.	Glazing: 1/8 inch (3 mm) DSB sheet glass.
b.	Glazing: 1/8 inch (3 mm) acrylic sheet.
c.	Glazing: 1/2 inch (12 mm) insulated glass glazing.
14.	PVC Windows (WxH): 12 x 40.5 inches (305 x 1029 mm):
a.	Glazing: 1/8 inch (3 mm) DSB sheet glass.
b.	Glazing: 1/8 inch (3 mm) acrylic sheet.
c.	Glazing: 1/2 inch (12 mm) insulated glass glazing.
15.	Lock Type: One inside slide lock.
16.	Lock Type: Two inside slide locks.
17.	Lock Type: Five pin cylinder lock with outside key. 
18.	Lock Type: No Lock
19.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
20.	Weatherstripping: Complete perimeter seals.
21.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
22.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
23.	Track configuration to maximize headroom available per plans.
24.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
2.7	STEEL DOORS WITH MINOR RIBS, THERMALLY-BROKEN, POLYSTYRENE INSULATED
A.	Clopay Model 3200. Heavy duty steel doors with minor ribs, thermally-broken, polystyrene insulated.
1.	Maximum Door Size (WxH): 24 ft, 2 inches x 24 ft (7.3 x 7.3 m).
2.	Overall Panel Thickness: 2 inches (51 mm).
3.	Steel Skin Thickness: Exterior: 24 gauge 0.022 inch (0.56 mm). Interior: 27 gauge 0.016 inch (0.40 mm) interior.
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Pre-painted steel. 0.049 inch (1.25 mm) thick. Easy hardware attachment through pre-punched holes.
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 9.1 deg F hr sq ft/Btu (1.6 (K sq m)/W).
8.	U-Factor: 0.23.
9.	Air Infiltration: 0.34 cfm at 25 mph.
10.	Windows: None.
11.	Windows (WxH): 8 x 24 inches (200 x 600 mm). Extruded polypropylene 
a.	Glazing: 1 inch (25 mm) insulated glass.
b.	Glazing: 1 inch (25 mm) insulated tempered glass.
12.	Windows (WxH): 12 x 24 inches (305 x 600 mm). Extruded polypropylene.
a.	Glazing: 1 inch (25 mm) insulated glass.
b.	Glazing: 1 inch (25 mm) insulated tempered glass.
13.	Windows: Full vision aluminum section, pre-painted to match door finish.
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass.
b.	Glazing: 1/4 inch (6 mm) tempered clear float glass.
c.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
d.	Glazing: Custom ________.
14.	Finish: Stucco embossed texture with 0.040 inch (100 mm) minor ribs 4 inches or 5 inches (100 or 125 mm) on center. Interior Color: White. 
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Commercial Tan.
d.	Exterior Color: Gray.
e.	Exterior Color: Black
f.	Exterior Color: Trinar White.
g.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
15.	Lock Type: One inside slide lock.
16.	Lock Type: Two inside slide locks.
17.	Lock Type: Five pin cylinder lock with outside key. 
18.	Lock Type: No Lock
19.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
20.	Weatherstripping: Complete perimeter seals.
21.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
22.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
23.	Track configuration to maximize headroom available per plans.
24.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
25.	Break-Away Bottom Section: Integral part of door. Fiberglass with flexible neoprene rubber side edges. Exterior to match door face. 
a.	Single Breakaway Bottom Section: For doors up to 20 ft (6 m) wide. 
b.	Double Breakaway Bottom Section: For doors up to 14 ft (4.3 m) wide. 
26.	Pass Door (Walk-Through Service Door): 32 x 80 inches (813 x 2032 mm) with aluminum frame, geared hinge, and pneumatic door closer; exterior matching door face; integral shiplap weather seal; keyed dead latch security lock.
B.	Clopay Model 3150. Standard duty steel doors with minor ribs, thermally-broken, polystyrene insulated.
1.	Maximum Door Size (WxH): 18 ft 2 inches x 16 ft (5.54 x 4.88 m). 
2.	Overall Panel Thickness: 1-3/8 inches (35 mm). 
3.	Steel Skin Thickness: Exterior and Interior: 27 gauge, 0.016 inch (0.40 mm) 
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Pre-painted steel. 0.034 inch (0.86 mm) thick. Easy hardware attachment through pre-punched holes. 
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 6.5 deg F hr sq ft/Btu (1.15 (K sq m)/W).
8.	U-Factor: 0.27.
9.	Air Infiltration: 0.41 cfm at 25 mph.
10.	Windows: None.
11.	Windows (WxH): 8 x 24 inches (200 x 600 mm). Extruded polypropylene 
a.	Glazing: 1/2 inch (12 mm) insulated glass.
b.	Glazing: 1/2 inch (12 mm) insulated tempered glass.
12.	Windows (WxH): 12 x 24 inches (305 x 600 mm). Extruded polypropylene.
a.	Glazing: 1/2 inch (12 mm) insulated glass.
b.	Glazing: 1/2 inch (12 mm) insulated tempered glass.
13.	Windows: Full vision aluminum section, pre-painted to match door finish. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass.
b.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
c.	Glazing: Custom ________.
14.	Finish: Stucco embossed texture with 0.040 inch (100 mm) minor ribs 4 or 5 inches (100 or 125 mm) on center. Interior Color: White. 
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Commercial Tan.
d.	Exterior Color: Gray.
e.	Exterior Color: Charcoal.
f.	Exterior Color: Mocha Brown.
g.	Exterior Color: Glacier White.
h.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
15.	Lock Type: One inside slide lock.
16.	Lock Type: Two inside slide locks.
17.	Lock Type: Five pin cylinder lock with outside key. 
18.	Lock Type: No Lock
19.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
20.	Weatherstripping: Complete perimeter seals. 
21.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
22.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
23.	Track configuration to maximize headroom available per plans.
24.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles.
e.	Maximum cycles in a single shaft line.
2.8	FLUSH STEEL DOORS, THERMALLY-BROKEN, POLYSTYRENE INSULATED 
A.	Clopay Model 3220. Premium duty flush steel doors, thermally-broken, polystyrene insulated.
1.	Maximum Door Size (WxH): 28 ft 2 inches (8.6 m) wide by 24 ft (7.3 m) high. 
2.	Overall Panel Thickness: 2 inches (51 mm).
3.	Steel Skin Thickness: Exterior: 20 ga 0.034 inch (0.86 mm). Interior: 27 ga 0.016 inch (0.40 mm).
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Pre-painted steel. 0.049 inch (1.25 mm) thick. Easy hardware attachment through pre-punched holes. 
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 9.1 deg F hr sq ft/Btu (1.6 (K sq m)/W).
8.	U-Factor: 0.23.
9.	Air Infiltration: 0.34 cfm at 25 mph.
10.	Windows: None.
11.	Windows (WxH): 8 x 24 inches (200 x 600 mm). Extruded polypropylene.
a.	Glazing: 1 inch nominal (25 mm) insulated glass.
b.	Glazing: 1 inch nominal (25 mm) insulated tempered glass.
12.	Windows (WxH): 12 x 24 inches (305 x 600 mm). Extruded polypropylene.
a.	Glazing: 1 inch nominal (25 mm) insulated glass.
b.	Glazing: 1 inch nominal (25 mm) insulated tempered glass.
13.	Windows: Full vision aluminum section, pre-painted to match door finish.
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass.
b.	Glazing: 1/4 inch (6 mm) tempered clear float glass.
c.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
d.	Glazing: Custom ________.
14.	Finish: Stucco embossed texture. Interior Color: White.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
15.	Lock Type: One inside slide lock.
16.	Lock Type: Two inside slide locks.
17.	Lock Type: Five pin cylinder lock with outside key. 
18.	Lock Type: No Lock.
19.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
20.	Weatherstripping: Complete perimeter seals.
21.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
22.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
23.	Track configuration to maximize headroom available per plans.
24.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
25.	Break-Away Bottom Section: Integral part of door. Fiberglass with flexible neoprene rubber side edges. Exterior to match door face. 
a.	Single Breakaway Bottom Section: For doors up to 20 ft (6 m) wide. 
b.	Double Breakaway Bottom Section: For doors up to 14 ft (4.3 m) wide. 
26.	Pass Door (Walk-Through Service Door): 32 x 80 inches (813 x 2032 mm) with aluminum frame, geared hinge, and pneumatic door closer; exterior matching door face; integral shiplap weather seal; keyed dead latch security lock.
B.	Clopay Model 3211. Heavy duty flush woodgrain embossed steel doors, thermally-broken, polystyrene insulated.
1.	Maximum Door Size (WxH): 24 ft, 2 inches x 18 ft (7.4 x 5.5 m) high.
2.	Overall Panel Thickness: 2 inches (51 mm).
3.	Steel Skin Thickness: Exterior: 24 gauge 0.022 inch (0.56 mm). Interior: 27 gauge 0.016 inch (0.40 mm) interior.
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	Stiles: Pre-painted steel. 0.049 inch (1.25 mm) thick Easy hardware attachment through pre-punched holes.
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 9.1 deg F hr sq ft/Btu (1.6 (K sq m)/W).
8.	U-Factor: 0.23.
9.	Air Infiltration: 0.34 cfm at 25 mph.
10.	Windows: None.
11.	PVC Windows (WxH): 12 x 19-1/2 inches (305 x 495 mm):
a.	Glazing: 1/8 inch (3 mm) DSB sheet glass.
b.	Glazing: 1/8 inch (3 mm) acrylic sheet.
c.	Glazing: 1/2 inch (12 mm) insulated glass glazing.
12.	Finish: Flush exterior design with wood grain embossment. Interior Color: White.
a.	Exterior White.
b.	Exterior Brown.
c.	Exterior Almond. 
d.	Exterior Desert Tan. 
e.	Exterior Sandtone. 
f.	Exterior Trinar White. 
g.	Exterior Trinar Beige.
h.	Exterior Black
i.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
13.	Lock Type: One inside slide lock.
14.	Lock Type: Two inside slide locks.
15.	Lock Type: Five pin cylinder lock with outside key. 
16.	Lock Type: No Lock
17.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
18.	Weatherstripping: Complete perimeter seals. 
19.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
20.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
21.	Track configuration to maximize headroom available per plans.
22.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
C.	Clopay Model 3155. Standard duty flush woodgrain embossed steel doors, thermally-broken, polystyrene insulated.
1.	Maximum Door Size (WxH): 18 ft 2 inches x 16 ft (5.54 x 4.88 m). 
2.	Overall Panel Thickness: 1-3/8 inches (35 mm). 
3.	Steel Skin Thickness: Exterior and Interior: 27 gauge, 0.016 inch (0.40 mm) 
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Pre-painted steel. 0.034 inch (0.86 mm) thick. Easy hardware attachment through pre-punched holes. 
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 6.5 deg F hr sq ft/Btu (1.15 (K sq m)/W).
8.	U-Factor: 0.27.
9.	Air Infiltration: 0.41 cfm at 25 mph.
10.	Windows: None.
11.	PVC Windows (WxH): 12 x 19-1/2 inches (305 x 495 mm):
a.	Glazing: 1/8 inch (3 mm) DSB sheet glass.
b.	Glazing: 1/8 inch (3 mm) acrylic sheet.
c.	Glazing: 1/2 inch (12 mm) insulated glass glazing.
12.	Finish: Wood grained embossed texture with flush panel. Interior Color: White.
a.	Exterior White. 
b.	Exterior Brown. 
c.	Exterior Almond.
d.	Exterior Sandtone.
e.	Exterior Bronze.
f.	Exterior Gray.
g.	Exterior Hunter Green 
h.	Exterior Desert Tan 
i.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
13.	Lock Type: One inside slide lock.
14.	Lock Type: Two inside slide locks.
15.	Lock Type: Five pin cylinder lock with outside key. 
16.	Lock Type: No Lock
17.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
18.	Weatherstripping: Complete perimeter seals.
19.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
20.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
21.	Track configuration to maximize headroom available per plans.
22.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
2.9	RAISED PANEL STEEL DOORS, THERMALLY-BROKEN, POLYSTYRENE INSULATED
A.	Clopay Model 3213. Heavy duty raised panel wood grain embossed steel doors, thermally-broken, polystyrene insulated.
1.	Maximum Door Size (WxH): 24 ft, 2 inches s 18 ft (7.4 x 5.5 m).
2.	Steel Skin Thickness: Exterior: 24 gauge 0.022 inch (0.56 mm). Interior: 27 gauge 0.016 inch (0.40 mm) interior.
3.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
4.	End Stiles: Pre-painted steel. 0.049 inch (1.25 mm) thick. Easy hardware attachment through pre-punched holes. 
5.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
6.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 9.1 deg F hr sq ft/Btu (1.6 (K sq m)/W).
7.	U-Factor: 0.23.
8.	Air Infiltration: 0.34 cfm at 25 mph.
9.	Windows: None.
10.	PVC Windows (WxH): 12 x 19-1/2 inches (305 x 495 mm):
a.	Glazing: 1/8 inch (3 mm) DSB sheet glass.
b.	Glazing: 1/8 inch (3 mm) acrylic sheet.
c.	Glazing: 1/2 inch (12 mm) insulated glass glazing.
11.	Finish: Raised panel exterior design. Interior Color: White.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Almond.
d.	Exterior Color: Desert Tan.
e.	Exterior Color: Sandtone.
f.	Exterior Color: Trinar White.
g.	Exterior Color: Trinar Beige.
h.	Exterior Color: Black.
i.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
12.	Lock Type: One inside slide lock.
13.	Lock Type: Two inside slide locks.
14.	Lock Type: Five pin cylinder lock with outside key. 
15.	Lock Type: No Lock
16.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
17.	Weatherstripping: Complete perimeter seals.
18.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
19.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
20.	Track configuration to maximize headroom available per plans.
21.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
B.	Clopay Model 3154. Standard duty raised panel woodgrain embossed steel doors, thermally-broken, polystyrene insulated.
1.	Maximum Door Size (WxH): 18 ft 2 inches x 16 ft (5.54 x 4.88 m).
2.	Overall Panel Thickness: 1-3/8 inches (35 mm). 
3.	Steel Skin Thickness: Exterior and Interior: 27 gauge, 0.016 inch (0.40 mm) 
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	End Stiles: Pre-painted steel. 0.034 inch (0.86 mm) thick. Easy hardware attachment through pre-punched holes. 
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 6.5 deg F hr sq ft/Btu (1.15 (K sq m)/W).
8.	U-Factor: 0.27.
9.	Air Infiltration: 0.41 cfm at 25 mph.
10.	Windows: None.
11.	PVC Windows (WxH): 12 x 19-1/2 inches (305 x 495 mm):
a.	Glazing: 1/8 inch (3 mm) DSB sheet glass.
b.	Glazing: 1/8 inch (3 mm) acrylic sheet.
c.	Glazing: 1/2 inch (12 mm) insulated glass glazing.
12.	Finish: Wood grain embossed texture with 0.040 inch (100 mm) elegant, raised panel.
a.	Exterior Color: White. 
b.	Exterior Color: Brown.
c.	Exterior Color: Almond.
d.	Exterior Color: Sandtone.
e.	Exterior Color: Bronze.
f.	Exterior Color: Gray.
g.	Exterior Color: Desert Tan
h.	Exterior Color: Hunter Green
i.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
13.	Lock Type: One inside slide lock.
14.	Lock Type: Two inside slide locks.
15.	Lock Type: Five pin cylinder lock with outside key. 
16.	Lock Type: No Lock
17.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
18.	Weatherstripping: Complete perimeter seals.
19.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
20.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
21.	Track configuration to maximize headroom available per plans.
22.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
2.10	DEEP RIBBED STEEL DOORS, POLYSTYRENE INSULATED
A.	Clopay Model 520S. Premium Duty Deep ribbed steel polystyrene insulated doors.
1.	Maximum Door Size (WxH): 32 ft, 2 inches x 24 ft (9.8 x 7.3 m).
2.	Interior Backer Cover: Pre-painted 30 gauge steel.
3.	Exterior Steel Skin Thickness: 20 ga 0.034 inch (0.86 mm). 
4.	End Stiles: Galvanized, primed, and polyester top-coated turn-down steel. Easy hardware attachment through pre-punched holes.
5.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
6.	Insulation: 1-3/8 inches thick (35 mm) polystyrene insulation
7.	Thermal resistance (R-value) calculated in accordance with DASMA TDS-163: 6.6 hr sq ft deg F/BTU (1.2 K sq m/W).
8.	Windows: None.
9.	Windows (WxH): 24 x 6 inches (150 x 610 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
b.	Glazing: 1/2 inch (13 mm) dual pane insulated tempered glazing.
10.	Windows (WxH): 24 x 12 inches (610 x 300 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
b.	Glazing: 1/2 inch (13 mm) dual pane insulated tempered glazing.
11.	Windows: Full-view sections, pre-painted to match door finish. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass
b.	Glazing: 1/4 inch (6 mm) tempered clear float glass
c.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
d.	Glazing: Custom ________.
12.	Finish: Exterior: 1 mil (.025 mm) coating. Interior: 0.5 mil (0.013 mm) coating.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
13.	Lock Type: One inside slide lock.
14.	Lock Type: Two inside slide locks.
15.	Lock Type: Five pin cylinder lock with outside key. 
16.	Lock Type: No Lock
17.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
18.	Weatherstripping: Complete perimeter seals.
19.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
20.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
21.	Track configuration to maximize headroom available per plans.
22.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
B.	Clopay Model 524S. Heavy Duty Deep ribbed steel polystyrene insulated doors.
1.	Interior Backer Cover: Pre-painted 30 gauge steel.
2.	Maximum Door Size (WxH): 26 ft, 2 inches x 24 ft (7.97 x 7.31 m). 
3.	Exterior Steel Skin Thickness: 24 ga 0.022 inch (0.56 mm). 
4.	End Stiles: Galvanized, primed, and polyester top-coated turn-down steel. Easy hardware attachment through pre-punched holes.
5.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
6.	Insulation: 1-3/8 inches thick (35 mm) polystyrene insulation
7.	Thermal resistance (R-value) calculated in accordance with DASMA TDS-163: 6.6 hr sq ft deg F/BTU (1.2 K sq m/W).
8.	Windows: None.
9.	Windows (WxH): 24 x 6 inches (150 x 610 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
b.	Glazing: 1/2 inch (13 mm) dual pane insulated tempered glazing.
10.	Windows (WxH): 24 x 12 inches (610 x 300 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
b.	Glazing: 1/2 inch (13 mm) dual pane insulated tempered glazing.
11.	Windows: Full-view sections, pre-painted to match door finish. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass
b.	Glazing: 1/4 inch (6 mm) tempered clear float glass
c.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
d.	Glazing: Custom ________.
12.	Finish: Exterior: 1 mil (.025 mm) coating. Interior: 0.5 mil (0.013 mm) coating.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Tan.
d.	Exterior Color: Gray.
e.	Exterior Color: Trinar White.
f.	Clopay ColorBlast, a two part paint system utilizing Sherwin Williams Solar reflective Polane Paint system. Sherwin Williams color number SW ______.
13.	Lock Type: One inside slide lock.
14.	Lock Type: Two inside slide locks.
15.	Lock Type: Five pin cylinder lock with outside key. 
16.	Lock Type: No Lock
17.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
18.	Weatherstripping: Complete perimeter seals.
19.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
20.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
21.	Track configuration to maximize headroom available per plans.
22.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
C.	Clopay Model 524V. Heavy duty deep ribbed steel polystyrene insulated doors.
1.	Panel Sections: 2 inches (52 mm) thick roll formed commercial quality steel panel sections; hot-dip galvanized with interior polyethylene vinyl back cover.
2.	Exterior Steel Skin Thickness: Minimum 24 ga 0.022 inch (0.56 mm).
3.	Maximum Door Size (WxH): 26 ft, 2 inches x 24 ft (7.97 x 7.31 m). 
4.	End Stiles: Galvanized, primed, and polyester top-coated turn-down steel. Easy hardware attachment through pre-punched holes.
5.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
6.	Insulation: 1-3/8 inches thick (35 mm) polystyrene
7.	Thermal Resistance (R-value): 6.6 hr sq ft deg F/BTU (1.2 K sq m/W).
8.	Windows: None.
9.	Windows (WxH): 24 x 6 inches (150 x 610 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
b.	Glazing: 1/2 inch (13 mm) dual pane insulated tempered glazing.
10.	Windows (WxH): 24 x 12 inches (610 x 300 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
b.	Glazing: 1/2 inch (13 mm) dual pane insulated tempered glazing.
11.	Windows: Full-view sections, pre-painted to match door finish. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass
b.	Glazing: 1/4 inch (6 mm) tempered clear float glass
c.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
d.	Glazing: Custom ________.
12.	Finish: Exterior: 1 mil (.025 mm) coating. Interior: 0.5 mil (0.013 mm) coating.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Tan
d.	Exterior Color: Gray
e.	Exterior Color: Trinar White.
f.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
13.	Lock Type: One inside slide lock.
14.	Lock Type: Two inside slide locks.
15.	Lock Type: Five pin cylinder lock with outside key.
16.	Lock Type: No lock.
17.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
18.	Weatherstripping: Complete perimeter seals.
19.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
20.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
21.	Track configuration to maximize headroom available per plans.
22.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
D.	Clopay Model 525S. Heavy duty deep ribbed steel polystyrene insulated doors.
1.	Maximum Door Size (WxH): 20 ft 2 inches x 18 ft (6.15 x 5.5 m).
2.	Interior Backer Cover: Pre-painted 30 gauge steel.
3.	Exterior Steel Skin Thickness: 25 ga 0.019 inch (0.48 mm).
4.	End Stiles: Galvanized, primed, and polyester top-coated turn-down steel. Easy hardware attachment through pre-punched holes.
5.	Insulation: 1-3/8 inches thick (35 mm) polystyrene insulation 
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal resistance (R-value): 6.6 hr sq ft deg F/BTU (1.2 K sq m/W).
8.	Windows: None.
9.	Windows (WxH): 24 x 6 inches (150 x 610 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
b.	Glazing: 1/2 inch (13 mm) dual pane insulated tempered glazing.
10.	Windows (WxH): 24 x 12 inches (610 x 300 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
b.	Glazing: 1/2 inch (13 mm) dual pane insulated tempered glazing.
11.	Windows: Full-view sections, pre-painted to match door finish. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass
b.	Glazing: 1/4 inch (6 mm) tempered clear float glass
c.	Glazing: Custom ________.
12.	Finish: Exterior: 1 mil (0.025 mm) coating. Interior: 0.5 mil (0.013 mm) coating.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
13.	Lock Type: One inside slide lock.
14.	Lock Type: Two inside slide locks.
15.	Lock Type: Five pin cylinder lock with outside key. 
16.	Lock Type: No Lock
17.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
18.	Weatherstripping: Complete perimeter seals.
19.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
20.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
21.	Track configuration to maximize headroom available per plans.
22.	Torsion Spring Counterbalance: Mechanism sized to weight of door. Helically wound, oil tempered spring on steel shaft. Cable drum of die cast aluminum with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
E.	Clopay Model 525V. Heavy duty deep ribbed steel polystyrene insulated doors.
1.	Panel Sections: 2 inches (52 mm) thick roll formed commercial quality steel panel sections; hot-dip galvanized with interior polyethylene vinyl back cover.
2.	Maximum Door Size (WxH): 20 ft 2 inches x 18 ft (6.15 x 5.5 m).
3.	End Stiles: Galvanized, primed, and polyester top-coated turn-down steel. Easy hardware attachment through pre-punched holes.
4.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
5.	Exterior Steel Skin Thickness: 25 ga 0.019 inch (0.48 mm). 
6.	Insulation: 1-3/8 inches thick (35 mm) polystyrene insulation
7.	Thermal Resistance (R-value): 6.6 hr sq ft deg F/BTU (1.2 K sq m/W).
8.	Windows: None.
9.	Windows (WxH): 24 x 6 inches (150 x 610 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
b.	Glazing: 1/2 inch (13 mm) dual pane insulated tempered glazing.
10.	Windows (WxH): 24 x 12 inches (610 x 300 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
b.	Glazing: 1/2 inch (13 mm) dual pane insulated tempered glazing.
11.	Windows: Full-view sections, pre-painted to match door finish. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass
b.	Glazing: 1/4 inch (6 mm) tempered clear float glass
c.	Glazing: Custom ________.
12.	Finish: Exterior: 1 mil (.025 mm) coating. Interior: 0.5 mil (0.013 mm) coating.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
13.	Lock Type: One inside slide lock.
14.	Lock Type: Two inside slide locks.
15.	Lock Type: Five pin cylinder lock with outside key. 
16.	Lock Type: No Lock.
17.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
18.	Weatherstripping: Complete perimeter seals.
19.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
20.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
21.	Track configuration to maximize headroom available per plans.
22.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles.
e.	Maximum cycles in a single shaft line.
2.11	FLUSH STEEL DOORS, POLYSTYRENE INSULATED
A.	Clopay Model 522S. Premium duty flush steel polystyrene insulated doors.
1.	Maximum Door Size (WxH): 24 ft, 2 inches x 24 ft (7.37 x 7.32 m). 
2.	Interior Backer Cover: Pre-painted 30 gauge steel.
3.	Exterior Steel Skin Thickness: 20 ga 0.034 inch (0.86 mm).
4.	End Stiles: Galvanized, primed, and polyester top-coated turn-down steel. Easy hardware attachment through pre-punched holes.
5.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
6.	Insulation: 1-3/8 inches thick (35 mm) polystyrene insulation
7.	Thermal resistance (R-value): 6.6 hr sq ft deg F/BTU (1.2 K sq m/W)
8.	Windows: None.
9.	Windows (WxH): 24 x 6 inches (150 x 610 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
b.	Glazing: 1/2 inch (13 mm) dual pane insulated tempered glazing.
10.	Windows (WxH): 24 x 12 inches (610 x 300 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
b.	Glazing: 1/2 inch (13 mm) dual pane insulated tempered glazing.
11.	Windows: Full-view sections, pre-painted to match door finish. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass
b.	Glazing: 1/4 inch (6 mm) tempered clear float glass
c.	Glazing: 1/2 inch (13 mm) dual pane insulated glazing.
d.	Glazing: Custom ________.
12.	Finish: Exterior: 1 mil (.025 mm) coating. Interior: 0.5 mil (0.013 mm) coating.
a.	Exterior Color: White. 
b.	Exterior Color: Brown. 
13.	Lock Type: Provide one inside slide lock. 
14.	Lock Type: Provide two inside slide lock. 
15.	Lock Type: Provide five pin cylinder lock with outside key. 
16.	Lock Type: No lock
17.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
18.	Weatherstripping: Complete perimeter seals.
19.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
20.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
21.	Track configuration to maximize headroom available per plans.
22.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
2.12	RAISED PANEL STEEL DOORS, POLYSTYRENE INSULATED 
A.	Clopay Model 664V. Heavy duty steel woodgrain embossed raised panel steel door. Polystyrene insulation with vinyl back cover.
1.	Maximum Door Size (WxH): 20 ft x 18 ft (6.10 x 5.49 m). 
2.	Overall Panel Thickness: 2 inches (51 mm). 
3.	Exterior Skin Thickness: 24 ga 0.022 inch (0.56 mm) exterior. 
4.	Interior Skin: Polyethylene vinyl backer. Color: White. 
5.	End Stiles: Pre-painted steel.
a.	Up to 16 ft - 2 inches (4.9 m) Wide: 18 ga 0.049 inch (1.25 mm) thick.
b.	Over 16 ft - 2 inches (4.9 m) Wide: Double end stile of one 18 ga 0.049 inch (1.25 mm) plus one 20 ga 0.035 inch (.89 mm) center stile. 
6.	Astragal: U-shaped flexible PVC in full-length retainer of 0.055 inch (1.4 mm) rigid PVC.
7.	Thermal Resistance (R-value) calculated in accordance with DASMA TDS-163: 6.3 deg F hr sq ft/Btu (1.1 (K sq m)/W).
8.	Windows: None.
9.	PVC Windows (WxH): 12 x 19-1/2 inches (305 x 495 mm):
a.	Glazing: 1/8 inch (3 mm) DSB sheet glass.
b.	Glazing: 1/8 inch (3 mm) acrylic sheet.
c.	Glazing: 1/2 inch (12 mm) insulated glass glazing.
10.	Finish: Raised panel wood grain exterior design, pre-finished exterior with 1 mil, three coat baked-on polyester topcoat over primer on a phosphate coating. 
a.	Exterior Color: White. 
b.	Exterior Color: Brown
c.	Exterior Color: Almond. 
d.	Exterior Color: Desert Tan. 
e.	Exterior Color: Sandtone.
f.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
11.	Lock Type: Five pin cylinder lock with outside key. 
12.	Lock Type: Inside spring loaded slide bolt lock on end stile that engages slot in track. 
13.	Lock Type: No Lock
14.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
15.	Weatherstripping: Complete perimeter seals.
16.	Hinge and Roller Assemblies: Hinges and Brackets: 14 ga 0.070 inch (1.78 mm) galvanized steel. Ten, full-floating ball bearing steel rollers; case hardened steel bearing races. Mounted to fit track taper.
17.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
18.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
19.	Track configuration to maximize headroom available per plans.
20.	Torsion Spring Counterbalance: Low stress, helically wound, oil-tempered spring on galvanized steel tube or solid steel shaft. Die cast aluminum. Pre-formed galvanized steel aircraft cable. 7 to 1 safety factor. 
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
B.	Door Construction: 
1.	Panels: Steel woodgrain embossed raised panel steel door. Polystyrene insulation with vinyl back cover. 
2.	Steel Skin: Roll formed commercial or drawing quality steel sheet, hot-dip galvanized per ASTM A924/A924M and ASTM A653/A653M, pre-painted with primer and baked-on polyester topcoat. 
3.	Section Joints: Panel sections form a weather-tight tongue and groove joint. 
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	Handle: 3 inch (76 mm) horizontal galvanized steel step plate / lift handle located on bottom section. 
2.13	DEEP RIBBED STEEL DOORS, NON-INSULATED
A.	Clopay Model 520. Premium duty deep ribbed steel doors, non-insulated.
1.	Maximum Door Size (WxH): 32 ft, 2 inches x 24 ft (9.8 x 7.3 m).
2.	Steel Skin Thickness: 20 ga 0.034 inch (0.86 mm). 
3.	Windows: None.
4.	Windows (WxH): 24 x 6 inches (610 x 150 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass.
b.	Glazing: 1/8 inch (3 mm), tempered clear float glass
c.	Glazing: 1/8 inch (3 mm) acrylic glazing.
5.	Windows (WxH): 24 x 12 inches (610 x 300 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass.
b.	Glazing: 1/8 inch (3 mm), tempered clear float glass.
c.	Glazing: 1/8 inch (3 mm) acrylic glazing.
6.	Windows: Full-view sections, pre-painted to match door finish. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass
b.	Glazing: 1/4 inch (6 mm) tempered clear float glass
c.	Glazing: Custom: __________
7.	Finish: Exterior: 1 mil (.025 mm) coating. Interior: 0.5 mil (0.013 mm) coating.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
8.	Lock Type: One inside slide lock.
9.	Lock Type: Two inside slide locks.
10.	Lock Type: Five pin cylinder lock with outside key. 
11.	Lock Type: No Lock
12.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
13.	Weatherstripping: Complete perimeter seals. 
14.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
15.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
16.	Track configuration to maximize headroom available per plans.
17.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
B.	Clopay Model 524. Heavy duty deep ribbed steel doors, non-insulated.
1.	Maximum Door Size (WxH): 26 ft 2 inches x 24 ft (7.97 x 7.31 m).
2.	Steel Skin Thickness: 24 ga 0.022 inch (0.56 mm).
3.	Windows: None.
4.	Windows (WxH): 24 x 6 inches (150 x 610 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass.
b.	Glazing: 1/8 inch (3 mm), tempered clear float glass
c.	Glazing: 1/8 inch (3 mm) acrylic glazing.
5.	Windows (WxH): 24 x 12 inches (610 x 300 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass.
b.	Glazing: 1/8 inch (3 mm), tempered clear float glass.
c.	Glazing: 1/8 inch (3 mm) acrylic glazing.
6.	Windows: Full-view sections, pre-painted to match door finish. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass
b.	Glazing: 1/4 inch (6 mm) tempered clear float glass
c.	Glazing: Custom: __________
7.	Finish: Exterior: 1 mil (.025 mm) coating. Interior: 0.5 mil (0.013 mm) coating.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color: Commercial Tan.
d.	Exterior Color: Gray.
e.	Exterior Color: Trinar White.
f.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
8.	Lock Type: One inside slide lock.
9.	Lock Type: Two inside slide locks.
10.	Lock Type: Five pin cylinder lock with outside key. 
11.	Lock Type: No Lock
12.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
13.	Weatherstripping: Complete perimeter seals.
14.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
15.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
16.	Track configuration to maximize headroom available per plans.
17.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
C.	Clopay Model 525. Standard duty deep ribbed steel doors, non-insulated.
1.	Maximum Door Size (WxH): 20 ft 2 inches x 18 ft (6.15 x 5.5 m). 
2.	Steel Skin Thickness: 25 gauge 0.019 inch (0.48 mm). 
3.	Windows: None.
4.	Windows (WxH): 24 x 6 inches (610 x 150 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass.
b.	Glazing: 1/8 inch (3 mm), tempered clear float glass
c.	Glazing: 1/8 inch (3 mm) acrylic glazing.
5.	Windows (WxH): 24 x 12 inches (300 x 610mm). Polypropylene frame to match door color. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass.
b.	Glazing: 1/8 inch (3 mm), tempered clear float glass.
c.	Glazing: 1/8 inch (3 mm) acrylic glazing.
6.	Windows: Full-view sections, pre-painted to match door finish. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass
b.	Glazing: 1/4 inch (6 mm) tempered clear float glass
c.	Glazing: Custom: __________
7.	Finish: Exterior: 1 mil (.025 mm) coating. Interior: 0.5 mil (0.013 mm) coating.
a.	Exterior Color: White.
b.	Exterior Color: Brown.
c.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
8.	Lock Type: One inside slide lock.
9.	Lock Type: Two inside slide locks.
10.	Lock Type: Five pin cylinder lock with outside key. 
11.	Lock Type: No Lock
12.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
13.	Weatherstripping: Complete perimeter seals.
14.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
15.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
16.	Track configuration to maximize headroom available per plans.
17.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
D.	Door Construction:
1.	Panel Sections: 2 inch (52 mm) thick.
2.	Steel Skin: Roll formed commercial quality steel sheet, hot-dip galvanized per ASTM A924/A924M and ASTM A653/A653M, phosphatized and pre-painted with primer and baked-on polyester topcoat. 
3.	Panel Face Reinforcement: Two, 1/2 inch (13 mm) deep ribs on 8 inches (200 mm) centers, complemented by six, 1/8 inch (3 mm) beads on 2 inch (50 mm) centers. 
4.	Section Joints: Panel sections form a weathertight tongue and groove joint Bottom Panel Section: Reinforced with continuous 0.050 inch (1.27 mm) aluminum astragal retainer with U-shaped flexible PVC astragal.
5.	Door End Stiles: Galvanized, primed, and polyester top-coated turn-down steel end stiles. Wrap face of panel sections a full 1-3/8 inches (35 mm).
a.	Engineered for easy hardware attachment through pre-punched holes.
b.	For Door Widths up to 14 ft 2 inches (4.32 m): 0.049 inch (1.25 mm) thick.
c.	For Door Widths greater than 14 ft 2 inches (4.32 m): 0.61 inch (1.55 mm) thick.
6.	Connections: Fasten panel sections and stiles with manufacturer's Tog-L-Loc joining system.
2.14	FLUSH STEEL DOORS, NON-INSULATED
A.	Clopay Model 522. Premium Duty Flush steel doors, non-insulated.
1.	Maximum Door Size (WxH): 24 ft, 2 inches x 24 ft (7.37 x 7.32 m).
2.	Steel Skin Thickness: 20 gauge 0.034 inch (0.86 mm).
3.	Windows: None.
4.	Windows (WxH): 24 x 6 inches (610 x 150 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass.
b.	Glazing: 1/8 inch (3 mm), tempered clear float glass
c.	Glazing: 1/8 inch (3 mm) acrylic glazing.
5.	Windows (WxH): 24 x 12 inches (610 x 300 mm). Polypropylene frame to match door color. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass.
b.	Glazing: 1/8 inch (3 mm), tempered clear float glass.
c.	Glazing: 1/8 inch (3 mm) acrylic glazing.
6.	Windows: Full-view sections, pre-painted to match door finish. 
a.	Glazing: 1/8 inch (3 mm) DSB clear float glass
b.	Glazing: 1/4 inch (6 mm) tempered clear float glass
c.	Glazing: Custom: __________
7.	Finish: Interior: 0.5 mil (0.013 mm) coating. Exterior: 1 mil (.025 mm) coating. Exterior color as follows: 
a.	Color: White. 
b.	Color: Brown. 
8.	Lock Type: One inside slide lock.
9.	Lock Type: Two inside slide locks.
10.	Lock Type: Five pin cylinder lock with outside key. 
11.	Lock Type: No Lock
12.	Door Drop Safety Device: Brackets to stop door from falling if lift cables fail. 
13.	Weatherstripping: Complete perimeter seals.
14.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
15.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
16.	Track configuration to maximize headroom available per plans.
17.	Torsion Spring Counterbalance: Mechanism sized to weight of door, with high strength galvanized aircraft cable. 7 to 1 safety factor.
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
B.	Door Construction:
1.	Panel Sections: 2 inch (52 mm) thick.
2.	Steel Skin: Roll formed commercial quality steel sheet, hot-dip galvanized per ASTM A924/A924M and ASTM A653/A653M, phosphatized and pre-painted with primer and baked-on polyester topcoat. 
3.	Panel Face Reinforcement: Two, 1/2 inch (13 mm) deep ribs on 8 inches (200 mm) centers, complemented by six, 1/8 inch (3 mm) beads on 2 inch (50 mm) centers. 
4.	Section Joints: Panel sections form a weathertight tongue and groove joint Bottom Panel Section: Reinforced with continuous 0.050 inch (1.27 mm) aluminum astragal retainer with U-shaped flexible PVC astragal.
5.	Door End Stiles: Galvanized, primed, and polyester top-coated turn-down steel end stiles. Wrap face of panel sections a full 1-3/8 inches (35 mm).
a.	Engineered for easy hardware attachment through pre-punched holes.
b.	For Door Widths up to 14 ft 2 inches (4.32 m): 0.049 inch (1.25 mm) thick.
c.	For Door Widths greater than 14 ft 2 inches (4.32 m): 0.61 inch (1.55 mm) thick.
6.	Connections: Fasten panel sections and stiles with manufacturer's Tog-L-Loc joining system.
2.15	RAISED PANEL STEEL DOORS, NON-INSULATED
A.	Clopay Model 664. Heavy duty raised panel steel doors, non-insulated.
1.	Maximum Door Size (WxH): 20 ft x 18 ft (6.10 x 5.49 m). 
2.	Exterior Skin Thickness: 24 gauge 0.022 inch (0.56 mm). 
3.	Interior Finish of Exterior Skin: White.
4.	End Stiles: Pre-painted steel.
a.	For Door Widths up to 16 ft 2 inches (4.9 m): 18 ga 0.049 inch (1.25 mm) thick.
b.	For Door Widths over 16 ft 2 inches (4.9 m): Provide double end stiles composed of one 18 ga 0.049 inch (1.25 mm) plus one 20 ga 0.035 inch (0.89 mm) center stile. 
5.	Windows: None.
6.	PVC Windows (WxH): 12 x 19-1/2 inches (305 x 495 mm):
a.	Glazing: 1/8 inch (3 mm) DSB sheet glass. 
b.	Glazing: 1/8 inch (3 mm) clear acrylic sheet. 
c.	Glazing: 1/8 inch (3 mm) obscure sheet glass. 
7.	Finish: Raised panel wood grain exterior design, pre-finished exterior with 1-mil, three coat baked-on polyester topcoat over primer on a phosphate coating. 
a.	Exterior Color: White.
b.	Exterior Color: Almond.
c.	Exterior Color: Desert Tan.
d.	Exterior Color: Sandtone.
e.	Exterior Color: Brown.
f.	Exterior Color Blast. 
1)	SW Color Code No: _______. 
2)	SW Color Name: ________.
8.	Lock Type: No Lock
9.	Lock Type: Four point cylinder lock with L-handle and a single lock bar. 
10.	Door Drop Safety Device: Provide brackets designed to stop the fall of the door should lift cables fail.
11.	Weatherstripping: Complete perimeter seals.
12.	Hinge and Roller Assemblies: Hinges and Brackets: 14 ga 0.070 inch (1.78 mm) galvanized steel. Ten, full-floating ball bearing steel rollers; case hardened steel bearing races. Mounted to fit track taper.
13.	Track Size: 2 inches (51 mm) track for 2 inch (51 mm) diameter rollers.
a.	Vertical Tracks: 0.061 inch (1.55 mm) galvanized steel. 
b.	Horizontal Tracks 0.075 inch (1.91 mm) galvanized steel.
14.	Track Size: 3 inches (76 mm) track for 3 inch (76 mm) diameter rollers.
a.	Vertical and Horizontal Tracks: 0.096 inch (2.43 mm) galvanized steel.
15.	Track configuration to maximize headroom available per plans.
16.	Torsion Spring Counterbalance: Low stress, helically wound, oil-tempered spring on galvanized steel tube or solid steel shaft. Die cast aluminum. Pre-formed galvanized steel aircraft cable. 7 to 1 safety factor. 
a.	Standard Cycle Spring: 10,000 cycles.
b.	High Cycle Spring: 25,000 cycles.
c.	High Cycle Spring: 50,000 cycles.
d.	High Cycle Spring: 100,000 cycles
e.	Maximum cycles in a single shaft line.
B.	Door Construction:
1.	Panels: Steel embossed woodgrain raised panel steel door.
2.	Steel Skin: Formed from roll formed commercial or drawing quality steel sheet, hot-dip galvanized per ASTM A924/A924M and ASTM A653/A 53M, pre-painted with primer and baked-on polyester topcoat.
3.	Section Joint: Sections to form a weather-tight tongue and groove joint.
4.	Steel Reinforcement: Galvanized and primed. Located under each hinge location. Pre-punched for hinge attachment.
5.	Handle: 3 inch (76 mm) horizontal galvanized steel step plate / lift handle located on bottom section.
6.	Delete article if not required.
2.16	ELECTRIC DOOR OPERATORS
A.	Electric Door Operator: Comply with NFPA 70. Provided by door manufacturer with operational life specified complete with electric motor and factory pre-wired motor controls, starter, gear-reduction unit, clutch, remote-control stations, control devices, integral gearing for locking door, and accessories required for proper operation. 
1.	Design Operator to allow motor to be removed without disturbing limit switch adjustment and without affecting emergency auxiliary operator.
2.	Solenoid-operated brake.
B.	Disconnect Device: Hand-operated for emergency manual operation while disconnecting motor, without affecting timing of limit switch. Mount disconnect and operator accessible from floor level. Interlock device automatically prevents motor from operating when emergency operator is engaged.
C.	Control Equipment: Comply with NEMA ICS1, NEMA ICS 2, and NEMA ICS 6, with NFPA 70 Class 2 control circuit, maximum 24 V, AC or DC.
D.	Electric Motors: High-starting torque, reversible, continuous-duty, Class A insulated, electric motor, complying with NEMA MG 1, with overload protection, sized to start, accelerate, and operate door in either direction, from any position, at not less than 2/3 fps (0.2 m/s) and not more than 1 fps (.03m/s), without exceeding nameplate ratings or considering service factor.
1.	Reference Electrical Schedules for phase and voltage per location.
2.	Provide horsepower in accordance with manufacturer recommendations per door size and type.
E.	Remote Control Station: Continuous contact, 3-button control station with push - button controls labeled "Open", "Close" and "Stop".
1.	Interior units, fully guarded, surface mounted, heavy-duty type, with general-purpose NEMA ICS 6 enclosure in one of the following types:
a.	Enclosure Type: Type 1.
b.	Enclosure Type: Type 4.
c.	Enclosure Type: Type 12.
F.	Obstruction Detection Device: For full width of the door opening. Each motorized door to have external automatic safety sensor. Activation of sensor immediately stops and reverses downward door travel.
1.	Sensor Edge: Automatic safety sensing edge, located within astragal or weather stripping mounted to bottom bar. Contact with sensor immediately stops and reverses downward door travel. Connect to control circuit using manufacturer's standard take-up reel or self-coiling cord. 
2.	Sensing Edge Operation:
a.	Electric.
b.	Pneumatic.
c.	Electric fail safe.
d.	Pneumatic fail safe.
e.	Photo-electric control: Provide each motorized door with a photo-electric device that will stop and reverse the downward door travel if the light beam is broken or blocked. Device shall be:
1)	NEMA Type 1.
2)	NEMA Type 4.
G.	Limit Switches: Adjustable switches, interlocked with motor controls and set to automatically stop door at fully opened and fully closed positions.
H.	Radio Controls: 3 button radio transmitter providing remote open, close, stop functionality. External antenna and coaxial wiring to receiver enhancing radio control reception.
I.	Auxiliary Chain Hoist: For emergency manual operation while disconnecting motor, without affecting timing of limit switch. Disconnect and operator to be accessible from floor level. Interlock Device: Automatically prevents motor from operating when emergency operator is engaged.
PART 3    EXECUTION
3.1	EXAMINATION
A.	Examine wall and overhead areas, including opening framing and blocking, with installer present, for compliance with requirements for installation tolerances, clearances, and other conditions affecting performance of Work in this Section.
B.	If substrate preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.
3.2	PREPARATION
A.	Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.
3.3	INSTALLATION
A.	Install overhead doors and track in accordance with approved shop drawings and the manufacturer's printed instructions.
3.4	PROTECTION
A.	Protect installed products until completion of project.
B.	Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION