SECTION 14 10 00

DUMBWAITERS, MATERIAL LIFTS, AND VERTICAL RECIPROCATING CONVEYORS

Display hidden notes to specifier. (Don't know how? Click Here) 
 Copyright 2025 -  2025 ARCAT, Inc. - All rights reserved

PART 1    GENERAL
1.1	SECTION INCLUDES
A.	Dumbwaiters.
B.	Material lifts.
C.	Vertical Reciprocating Conveyors (VRCs).
1.2	RELATED SECTIONS
A.	Section 03 30 00 - Cast-in-Place Concrete.
B.	Section 04 20 00 - Unit Masonry.
C.	Section 06 11 00 - Wood Framing.
D.	Section 09 21 16.33 - Gypsum Board Area Separation Wall Assemblies.
E.	Section 05 50 00 - Metal Fabrications. All bracket fastening inserts and other steel required for support of guide rails and brackets.
F.	Section 09 90 00 - Painting and Coating. Painting of exterior walls and prime finished components that are exposed to view, including inside of car, car gates and doors.
G.	Section 26 00 00 - Electrical. A power line from the source to an approved 30 ampere fused disconnect switch located immediately adjoining the controller cabinet must be provided. A 110V single phase machine area lighting and convenience outlet must also be provided.
1.3	REFERENCES
A.	American Society of Mechanical Engineers (ASME):
1.	ASME A17.1/CSA B44 - Safety Code for Elevators and Escalators.
2.	ASME A17.2/CSA B44 - Inspector's Manual for Electric Elevators.
3.	ASME A17.5/CSA B44 - Elevator and Escalator Electrical Equipment.
4.	ASME/UL - 10B Fire Tests of Door Assemblies.
5.	ASME/UL - 508 Industrial Controllers.
B.	National Fire Protection Association (NFPA):
1.	NFPA 70 - National Electrical Code.
C.	Underwriters Laboratories (UL):
1.4	SUBMITTALS
A.	Submit under provisions of Section 01 30 00.
B.	Product Data:
1.	Manufacturer's data sheets on each product to be used.
2.	Preparation instructions and recommendations.
3.	Storage and handling requirements and recommendations.
4.	Typical installation methods.
C.	Verification Samples: Two representative units of each type, size, pattern, and color.
D.	Shop Drawings: Include details of materials, construction, and finish. Include relationship with adjacent construction. 
1.5	QUALITY ASSURANCE
A.	Manufacturer Qualifications: Company specializing in manufacturing products specified in this section with a minimum of five years documented experience.
B.	Installer Qualifications: Company specializing in performing Work of this section with minimum two years documented experience with projects of similar scope and complexity.
C.	Source Limitations: Provide each type of product from a single manufacturing source to ensure uniformity.
1.6	PRE-INSTALLATION CONFERENCE
A.	Convene a conference approximately two weeks before scheduled commencement of the Work. Attendees shall include Architect, Contractor and trades involved. Agenda shall include schedule, responsibilities, critical path items and approvals.
1.7	DELIVERY, STORAGE, AND HANDLING
A.	Store and handle in strict compliance with manufacturer's written instructions and recommendations.
B.	Protect from damage due to weather, excessive temperature, and construction operations.
1.8	PROJECT CONDITIONS
A.	Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's recommended limits.
1.9	WARRANTY
A.	Manufacturer's standard limited warranty unless indicated otherwise.
PART 2    PRODUCTS
2.1	MANUFACTURERS
A.	Acceptable Manufacturer: MATOT a division of Savaria, which is located at:<BR />2 Walker Dr.<BR />Brampton, ON, Canada L6T 5E1<BR />Toll Free Tel: 855-728-2742<BR />Fax: 905-791-2222<BR />Email: request info (sales@matot.com);Web: https://www.matot.com 
B.	Substitutions: Not permitted.
C.	Requests for substitutions will be considered in accordance with the provisions of Section 01 60 00.
2.2	DUMBWAITERS
A.	Basis of Design: Matot Dumbwaiters as manufactured by Savaria.
1.	When not indicated otherwise, provide manufacture's product as indicated in published product literature and as required for complete Savaria Matot Dumbwaiter systems.
B.	Performance and Design Requirements:
1.	Comply with applicable building and elevator codes at the project site, including but not limited to:
a.	ASME A17.1/CSA B44 - Safety Code for Elevators and Escalators.
b.	ASME A17.2/CSA B44 - Inspector's Manual for Electric Elevators.
c.	ASME A17.5/CSA B44 - Elevator and Escalator Electrical Equipment.
d.	NFPA 70 - National Electrical Code.
e.	ASME/UL - 10B Fire Tests of Door Assemblies.
f.	ASME/UL - 508 Industrial Controllers.
2.	Dumbwaiter Maximum Car Size per ANSI A17.1: 10.76 sq ft (1 sq m) x 48 inches (1219 mm) high.
3.	Inside Car Dimensions: 24 x 24 x 36 inches (610 x 610 x 914 mm).
4.	Inside Car Dimensions: 36 x 36 x 48 inches (914 x 914 x 1219 mm).
5.	Inside Car Dimensions: ___ x ___ x ___ inches (___ x ___ x ___ mm).
6.	Minimum Capacity: 13.9 lbs per cu ft of car size. 
7.	Maximum Capacity: Up to 750 lbs (340 kg).
8.	Capacity:  ___ lbs (___kg). 
9.	Rated Load Both Car and Machine: 125 percent of capacity. 
10.	Loading Configuration: Single side.
11.	Loading Configuration: Opposite side.
12.	Loading Configuration: Adjacent side.
13.	Number of Stops: ___.
a.	Leveling Accuracy: Car floor to be within plus or minus 1/4 inch (6 mm) above or below the hoistway door sill.
b.	Dumbwaiter Stop: Counter height.
c.	Dumbwaiter Stop: Floor level.
14.	Number or Landing Entrances: ___.
15.	Hoistway Opening Configuration: Bi-parting doors and gates.
a.	Pit Depth: 30 inches (762 mm).
b.	Overhead Clearance: _____ inches (____ mm). 
c.	Drawbridge: Provides smooth entrance for wheeled carts; raised and lowered by opening and closing of car gate.
16.	Hoistway Opening Configuration: Slide-up doors and gates or swing doors.
a.	Pit Depth: 8 inches (203 mm).
b.	Overhead Clearance: _____ inches (_____ mm). 
17.	Travel Distance: ___ft ___ inches (___ mm).
18.	Travel Speed, Nominal for Winding Drum Machine:  50 fpm (0.25 mps).
19.	Travel Speed, Nominal for Traction Machine:  75 fpm (37.5 mps).
20.	Travel Speed, Nominal for Traction Machine:  ___ fpm (___ mps).
21.	Speed Variance: Plus or minus 10 percent of the rated speed regardless of load or direction.
22.	Power Supply: ____ Volts, 3 Phase, 60 Hertz.
23.	Power Supply: ____ Volts, ___ Phase, 60 Hertz.
C.	Fabrication:
1.	Car Enclosure: 16-gauge, 304 Stainless steel.
2.	Removable shelf.
3.	Electrical light fixture recessed in the ceiling.
4.	Reinforced Floor: For Floor loading models.
D.	Machine:
1.	Machine Type: Winding Drum.
2.	Machine Type: Traction.
3.	Motor: To be of ample horsepower to lift the rated load at the rated speed, with a high starting torque and low starting current.
4.	Brake: Spring applied and electrically released.
5.	Variable Frequency and Invertor-Based Drive Systems: Smooth travel and precise stopping and starting.
6.	Mounting Base: Structural steel.
a.	Location: Bottom.
b.	Location: Top.
E.	Hoistway Doors: To bear the Underwriters "B" label for 1-1/2 hours.
1.	Hollow Metal Door Panels: Welded unit wall frame, including jambs, trim and sill; manufactured with 16 gauge material.
2.	A door lock and contact or true interlock are to be provided on each door.
3.	Door Type: Vertical two panel bi-parting doors.
4.	Door Type: Vertical single panel slide-up doors.
5.	Door Type: Swing Doors.
6.	Door Operation: Powered.
7.	Door Operation: Manual.
8.	Door Finish: 304 Stainless Steel.
9.	Door Finish:  Galvannealed steel, paint ready.  
F.	Cab Doors: To bear the Underwriters "B" label for 1-1/2 hours. 
1.	Hollow Metal Door Panels:  Welded unit wall frame, including jambs, trim and sill; manufactured with 16 gauge material. 
2.	Door Type:  Vertical two panel bi-parting doors. 
3.	Door Type:  Vertical single panel slide-up doors. 
4.	Door Type:  Collapsible (accordion) gate. 
5.	Door Operation:  Powered. 
6.	Door Operation: Manual. 
7.	Door Finish:  304 stainless steel.
8.	Door Finish:  Black enamel painted. 
G.	Machine Access Door (WxH): 24 x 24 inches (610 x 610 mm). Hinged. At machine location for service and maintenance.
1.	Material: 16 gauge Stainless steel.
H.	Self-Supporting Tower: Components shall be carried on a self-contained, rigidly braced, structural steel angle tower extending full height of the hoistway.
I.	Guide Rails: Elevator grade 8 lbs. "Tee" rails, to guide the car. Mounted to the floor slabs and hoistway wall with brackets.
1.	Rail and Bracket Material: Steel.
J.	Controller: Wall-mounted type with lockable door.
1.	Location: On hoistway outer wall in sight of machine access door.
2.	Characteristics: Solid-state programmable and Underwriter's Laboratories, Inc. (UL) listed.
K.	Operational Control: Microprocessor-controlled automatic call and send operation.
1.	Pushbutton Station: One button for each level served to be furnished at each door.
a.	Each Level: Call the car or send it to any other level.
b.	Pushbuttons: Inoperative while car is in transit and for a few seconds after arrival at the selected level.
c.	Pushbuttons Faceplates: Stainless steel.
L.	Signals Devices:
1.	"Door Open" Call Buzzer: Sounds when a pushbutton is pressed and a hoistway door or car gate is open.
2.	"Car Here" Light and Chime: Located in each pushbutton station.
a.	Chime: Indicates car arrival.
b.	Light: Indicates car presence.
3.	Combination "Door Open" and "In-Use" Light: Located in each pushbutton station. Light illuminates when car is in transit and when a pushbutton is pressed and a hoistway door or gate is open.
4.	Door Open / Door Close Button: Furnished if power operated hoistway doors are furnished.
M.	Hoist Ropes: If winding drum machine; minimum of one galvanized aircraft-grade cable with safety factor per code.
N.	Hoist Ropes: If Traction machine; minimum (2, 1/4 inch x 8 x 19) traction steel cable with safety factor per code.
O.	Final Limit Stopping Devices: Provide per code.
P.	Guide Shoes: To be adjustable, renewable dry type.
Q.	Roller Guides: Provided on traction machines.
R.	Counterweight: Equal in weight to that of the car plus 40 percent of the rated capacity.
S.	Security Systems:
1.	Key locks.
2.	Keypads.
3.	Interfaces to external security systems.
2.3	MATERIAL LIFTS
A.	Basis of Design: Matot Material Lifts as manufactured by Savaria.
1.	When not indicated otherwise, provide manufacture's product as indicated in published product literature and as required for complete Savaria Matot Dumbwaiter systems.
B.	Performance and Design Requirements:
1.	Comply with applicable building and elevator codes at the project site, including but not limited to:
a.	NFPA 70 - National Electrical Code.
b.	ASME/UL - 10B Fire Tests of Door Assemblies.
c.	ASME/UL - 508 Industrial Controllers.
2.	Inside Car Dimensions: 36 x 36 x 60 inches (914 x 914 x 1524 mm).
3.	Inside Car Dimensions: 48 x 60 x 72 inches (1219 x 1524 x 1829 mm).
4.	Inside Car Dimensions: ___ x ___ x ___ inches (___ x ___ x ___ mm).
5.	Maximum Capacity: 2500 lbs (1134 kg). 
6.	Minimum Capacity:  50 lbs per sq ft of car size. 
7.	Capacity: ___ lbs (___kg).
8.	Loading Configuration: Single side.
9.	Loading Configuration: Opposite side.
10.	Number of Stops: ___.
11.	Number or Openings: ___.
12.	Car will stop at floor level.
13.	Hoistway Opening Configuration: Bi-parting doors and gates.
a.	Pit Depth: 50 percent of car height plus 6 inches (152 mm).
b.	Overhead Clearance: ____ inches (____ mm). 
c.	Drawbridge: Provides smooth entrance for wheeled carts; raised and lowered by opening and closing of car gate.
14.	Hoistway Opening Configuration: Slide-up doors and gates or swing doors.
a.	Pit Depth: 16 inches (407 mm).
b.	Overhead Clearance: ____ inches (____ mm). 
15.	Travel Distance: ___ft ___ inches (___ mm).
16.	Travel Speed, Nominal for Winding Drums:  40 fpm (0.20 mps).   
17.	Travel Speed, Nominal for Traction Machines:  75 fpm (0.38 mps). 
18.	Travel Speed, Nominal for Traction Machines:  ___ fpm (___ mps). 
19.	Travel Speed Variance: Plus or minus 10 percent of the rated speed regardless of load or direction.
20.	Power Supply: ____ Volts, 3 Phase, 60 Hertz.
C.	Fabrication:
1.	Car Enclosure: 16 gauge. Stainless steel.
2.	Electrical light fixture recessed in the ceiling.
3.	Reinforced Floor: For floor loading models.
D.	Machine:
1.	Machine Type: Winding Drum.
2.	Machine Type: Traction.
3.	Motor: To be of ample horsepower to lift the rated load at the rated speed, with a high starting torque and low starting current. 
4.	Brake: Spring applied and electrically released.
5.	Mounting Base: Structural steel.
a.	Location: Top of the shaft.
E.	Hoistway Doors: To bear the Underwriters "B" label for 1-1/2 hours.
1.	Hollow metal door panels and welded unit wall frame, including jambs, trim and sill. Manufactured with 16 gauge material.
2.	A door lock and contact or true interlock shall be provided on each door.
3.	Door Type: Vertical two panel bi-parting doors.
4.	Door Type: Vertical single panel slide-up doors.
5.	Door Type: Swing doors. 
6.	Doors Operation: Manual.
7.	Doors Operation: Powered.
8.	Door Finish: Stainless steel.
9.	Door Finish: Galvannealed steel, paint ready. 
F.	Cab Doors: To bear the Underwriters "B" label for 1-1/2 hours. 
1.	Hollow Metal Door Panels:  Welded unit wall frame, including jambs, trim and sill; manufactured with 16 gauge material. 
2.	Door Type:  Vertical two panel bi-parting doors. 
3.	Door Type:  Vertical single panel slide-up doors. 
4.	Door Type:  Collapsible (accordion) gate. 
5.	Door Operation:  Powered. 
6.	Door Operation: Manual. 
7.	Door Finish: 304 stainless steel.
8.	Door Finish:  Black enamel painted. 
G.	Machine Access Door (WxH): 24 x 24 inches (610 x 610 mm). Hinged. At machine location for service and maintenance. 
1.	Material: 16 gauge ________.
H.	Guide Rails: Elevator grade 8 lbs. Steel "Tee" rails furnished to guide the car. Mounted to the floor slabs and hoistway wall with steel brackets. 
I.	Controller: Wall-mounted type with lockable door.
1.	Location: On hoistway outer wall in sight of machine access door. 
2.	Characteristics: Solid-state programmable and Underwriter's Laboratories, Inc. (UL) listed.
J.	Operational Control: Microprocessor-controlled automatic call and send operation. 
1.	Pushbutton Station: One button for each level served to be furnished at each door. 
a.	Each Level: Call the car or send it to any other level.
b.	Pushbuttons: Inoperative while car is in transit and for a few seconds after arrival at the selected level.
c.	Pushbuttons Faceplates: Stainless steel.
K.	Signals Devices: 
1.	"Door Open" Call Buzzer: Sounds when a pushbutton is pressed and a hoistway door or car gate is open.
2.	"Car Here" Light and Chime: Located in each pushbutton station. 
a.	Chime: Indicates car arrival. 
b.	Light: Indicates car presence.
3.	Combination "Door Open" and "In-Use" Light: Located in each pushbutton station. Light illuminates when car is in transit and when a pushbutton is pressed and a hoistway door or gate is open.
4.	Door Open / Door Close Button: Furnished if power operated hoistway doors are furnished.
L.	Hoist Ropes: If winding drum machine. Minimum of two galvanized aircraft-grade cable with safety factor per code.
M.	Hoist Ropes: If Traction machine: Minimum (2, 1/4 inch x 8 x 19) traction steel cable with safety factor per code.
N.	Final Limit Stopping Devices: Provide per code.
O.	Guide Shoes: Roller Guides.
P.	Counterweight: Equal in weight to that of the car plus 40 percent of the rated capacity. 
Q.	Security Systems:
1.	Key locks.
2.	Keypads.
3.	Interfaces to external security systems.
2.4	VERTICAL RECIPROCATING CONVEYORS (VRCS)
A.	Basis of Design: Matot Vertical Reciprocating Conveyors as manufactured by Savaria.
1.	When not indicated otherwise, provide manufacture's product as indicated in published product literature and as required for complete Matot VRC systems.
B.	Performance and Design Requirements:
1.	Comply with applicable building and conveyor codes at the project site, including but not limited to:
a.	ASME B20 - Safety Code for Vertical Reciprocating Conveyors.
b.	NFPA 70 - National Electrical Code.
c.	ASME/UL - 10B Fire Tests of Door Assemblies.
d.	ASME/UL - 508 Industrial Controllers.
2.	Inside Car Dimensions: 48 x 60 x 72 inches (1219 x 1524 x 1828 mm).
3.	Inside Car Dimensions: ___ x ___ x ___ inches (___ x ___ x ___ mm).
4.	Maximum Capacity: 2500 lbs (1134 kg).
5.	Minimum Capacity:  50 lbs per sq ft of car size. 
6.	Capacity: ___ lbs (___kg).
7.	Rated Load Both Car and Machine: 125 percent of capacity. 
8.	Loading Configuration: Single side.
9.	Loading Configuration: Opposite side.
10.	Number of Stops: ___.
a.	Leveling Accuracy: Car floor to be within plus or minus 1/4 inch above or below the hoistway door sill.
b.	VRC Stop: Floor level.
11.	Number of Openings: ___.
12.	Hoistway Opening Configuration: Bi-parting doors and gates.
a.	Pit Depth: 50 percent of car height plus 6 inches (152 mm).
b.	Overhead Clearance: ____ inches (____ mm). 
c.	Drawbridge: Provides smooth entrance for wheeled carts; raised and lowered by opening and closing of car gate. 
13.	Hoistway Opening Configuration: Slide-up doors and gates or swing gates.
a.	Pit Depth: 16 inches (407 mm).
b.	Overhead Clearance: ____ inches (____ mm). 
14.	The car shall stop at floor level.
15.	Travel Distance: ___ft ___ inches (___ mm).
16.	Travel Speed, Nominal for Winding Drums:  40 fpm (0.20 mps).
17.	Travel Speed, Nominal for Traction Machines:  75 fpm (0.38 mps). 
18.	Travel Speed Variance: Plus or minus 10 percent of the rated speed regardless of load or direction.
19.	Power Supply: ____ Volts, 3 Phase, 60 Hertz.
C.	Fabrication:
1.	Car Enclosure: 16 gauge. Stainless steel.
2.	Electrical light fixture recessed in the ceiling.
3.	Reinforced Floor: For floor loading models.
D.	Machine: 
1.	Machine Type:  Winding Drum. 
2.	Machine Type:  Traction. 
3.	Motor:  To be of ample horsepower to lift the rated load at the rated speed, with a high starting torque and low starting current. 
4.	Brake: Spring applied and electrically released.
5.	Mounting Base: Structural steel.
a.	Location: Top of the shaft.
E.	Hoistway Doors: To bear the Underwriters "B" label for 1-1/2 hours.
1.	Hollow metal door panels and welded unit wall frame, including jambs, trim and sill shall be manufactured with 16 gauge material
2.	A door lock and contact or true interlock shall be provided on each door.
3.	Door Type: Vertical two panel bi-parting doors.
4.	Door Type: Vertical single panel slide-up doors.
5.	Door Type: Swing doors. 
6.	Doors Operation: Manual.
7.	Doors Operation: Powered.
8.	Door Finish: 304 Stainless steel.
9.	Door Finish: Galvannealed steel, paint ready.
F.	Cab Doors: To bear the Underwriters "B" label for 1-1/2 hours. 
1.	Hollow Metal Door Panels:  Welded unit wall frame, including jambs, trim and sill; manufactured with 16 gauge material. 
2.	Door Type:  Vertical two panel bi-parting doors. 
3.	Door Type:  Vertical single panel slide-up doors. 
4.	Door Type:  Collapsible (accordion) gate. 
5.	Door Operation:  Powered. 
6.	Door Operation: Manual. 
7.	Door Finish:  304 stainless steel.
8.	Door Finish: Black enamel painted.
G.	Machine Access Door (WxH): 24 x 24 inches (610 x 610 mm). Hinged. At machine location for service and maintenance. 
1.	Material: 16 gauge ________.
H.	Guide Rails: Elevator grade 8 lbs. Steel "Tee" rails furnished to guide the car. Mounted to the floor slabs and hoistway wall with steel brackets. 
I.	Controller: Wall-mounted type with lockable door.
1.	Location: On hoistway outer wall in sight of machine access door. 
2.	Characteristics: Solid-state programmable and Underwriter's Laboratories, Inc. (UL) listed.
J.	Operational Control: Microprocessor-controlled automatic call and send operation. 
1.	Pushbutton Station: One button for each level served to be furnished at each door. 
a.	Each Level: Call the car or send it to any other level. 
b.	Pushbuttons: Inoperative while car is in transit and for a few seconds after arrival at the selected level. 
c.	Pushbuttons Faceplates: Stainless steel.
K.	Signals Devices: 
1.	"Door Open" Call Buzzer: Sounds when a pushbutton is pressed and a hoistway door or car gate is open.
2.	"Car Here" Light and Chime: Located in each pushbutton station. 
a.	Chime: Indicates car arrival. 
b.	Light: Indicates car presence.
3.	Combination "Door Open" and "In-Use" Light: Located in each pushbutton station. Light illuminates when car is in transit and when a pushbutton is pressed and a hoistway door or gate is open.
4.	Door Open / Door Close Button: Furnished if power operated hoistway doors are furnished.
L.	Hoist Ropes: 
1.	Winding Drum Machine: Minimum of two galvanized aircraft-grade cable with safety factor per code.
2.	Traction Machine: Minimum (2, 1/4 inch x 8 x 19) traction steel cable with safety factor per code.
M.	Final Limit Stopping Devices: Provide per code.
N.	Guide Shoes: Roller Guides.
O.	Counterweight: Equal in weight to that of the car plus 40 percent of the rated capacity. 
P.	Security Systems:
1.	Key locks.
2.	Keypads.
3.	Interfaces to external security systems.
PART 3    EXECUTION
3.1	EXAMINATION
A.	Do not begin installation until the substrates have been properly constructed and prepared.
1.	Verify hoistway and openings are of correct size and within tolerance. Verify electrical power is available and of correct characteristics.
B.	If substrate preparation is the responsibility of another installer, notify Architect in writing of unsatisfactory preparation before proceeding.
3.2	PREPARATION
A.	Clean surfaces thoroughly prior to installation.
B.	Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.
3.3	INSTALLATION
A.	Install in accordance with manufacturer's instructions, approved submittals, and in proper relationship with adjacent construction.
1.	Leave manufacturers electrical connection drawings with electrical contractor to make final electrical connection. 
2.	The installation of the Savaria Matot Material Lift shall be carried out in accordance with the approved plans and specifications and manufacture's installation instructions. 
3.	Do not begin installation until preliminary work, including hoistway, landings and machine space has been properly prepared.
4.	Coordinate installation of hoistway wall construction. 
5.	Check hoistway for plumb and square.
3.4	FIELD QUALITY CONTROL
A.	Field Inspection: Coordinate field inspection in accordance with appropriate sections in Division 01.
1.	Perform tests required by the manufacturer.
2.	Supply instruments and execute specific tests.
3.	Perform tests in presence of Architect:
4.	Test equipment by transporting the rated load up from main floor during thirty-minute period.
5.	At an agreed time during contract warranty period, and with building normally occupied using normal building traffic, conduct tests to verify performance.
6.	Time equipment travel between typical floors at not more than the rated travel time. 
B.	Field Services
1.	Obtain required permits to perform tests. Perform tests required by regulatory agencies. Schedule tests with agencies and Architect and Contractor present.
2.	Submit tests and approval certificates issued by jurisdictional authorities.
C.	Manufacturer's Services: Coordinate manufacturer's services in accordance with appropriate sections in Division 01.
1.	Engage a factory-authorized service representative to train Owner's maintenance personnel to operate installed equipment.
3.5	ADJUSTING, CLEANING AND PROTECTION
A.	Adjust for smooth and quiet movement of car and doors. Adjust for consistent stopping at landings.
B.	Protect installed products until completion of project.
C.	Remove protective coverings from finished surfaces. Clean surfaces and components ready for inspection in accordance with the manufacturers recommendations. 
D.	Touch-up, repair or replace damaged products before Substantial Completion.
3.6	DEMONSTRATION 
A.	Engage a factory-authorized service representative to train Owner's Maintenance personnel to operate the Matot Material Lift.

END OF SECTION