SECTION 23 51 00

BREECHINGS AND CHIMNEY LINERS

Display hidden notes to specifier. (Don't know how? Click Here)

Copyright 2023 -    2023 ARCAT, Inc. - All rights reserved

** NOTE TO SPECIFIER ** Z-Flex U.S. Inc.; Chimney Liners and Vents.
This section is based on the products of Z-Flex U.S. Inc., which is located at:<BR />20 Commerce Park N.<BR />Bedford, NH null<BR />Toll Free Tel: 800-654-5600<BR />Tel: 603-669-5136<BR />Fax: 603-669-0309<BR />Email: request info (mcreonte@z-flex.com)
Web: https://www.z-flex.com | https://www.novaflexgroup.com    
 [ Click Here ] for additional information.
Z-Flex U.S. Inc. is a leading manufacturer of high-quality venting systems for residential, commercial, and industrial applications. The company is based in Richmond Hill, Canada with 13 manufacturing plants in the United States, Canada, and the United Kingdom. Z-Flex has been in business for over forty years and is a Novaflex Group Company.
Z-Flex is committed to providing safe and efficient venting solutions for a variety of applications, including HVAC, boilers, pool heaters, water heaters, and more. The company's products are designed and manufactured to the highest standards, using only the highest-quality materials. Z-Flex stands apart from other venting companies with their focus on innovation. The company invests heavily in research and development, constantly striving to create new and better products that meet the evolving needs of their customers.
Known for their exceptional customer service, Z-Flex's team of experts is always available to answer questions and provide support for customers, ensuring that they have the information and resources necessary to make informed decisions about their venting needs. Overall, Z-Flex is a trusted and respected leader in the venting industry, known for their exceptional products, outstanding customer service, and commitment to sustainability.

- GENERAL

  - SECTION INCLUDES

** NOTE TO SPECIFIER ** Delete items below not required for project.

    - For Category I, II, III, IV Gas Fired Appliances:

      - Listed Single Wall Stainless Steel Vent. (Z-Vent Single Wal)

      - Listed Double Wall Stainless Steel Vent. (Z-Vent Double Wall)

      - Listed Smoothcore Flexible Stainless Steel Liner. (Z-Vent Smoothcore)

  - RELATED SECTIONS

** NOTE TO SPECIFIER ** Delete any sections below not relevant to this project; add others as required.

    - Section 04 50 00 - Refractory Masonry.

    - Section 10 30 00 - Fireplaces and Stoves.

    - Section 22 34 00 - Fuel-Fired Domestic Water Heaters

    - Section 23 50 00 - Central Heating Equipment

    - Section 23 52 00 - Heating Boilers

    - Section 23 54 00 - Furnaces

  - REFERENCES

** NOTE TO SPECIFIER ** Delete references from the list below that are not actually required by the text of the edited section.

    - American National Standards Institute (ANSI): USA

      - ANSI Z223.1/NFPA-54 - National Fuel Gas Code.

    - BOCA National Mechanical Code.

    - CSA Group (CSA): Canada

      - CSA B149.1 - Natural Gas and Propane Installation Code.

    - National Fire Protection Association (NFPA):

      - NFPA-54 - National Fuel Gas Code.

    - Standard Mechanical Code.

    - Underwriters Laboratories (UL):

      - UL 1738 - Venting Systems for Gas-Burning Appliances, Categories II, III, and IV.

      - ULC S636 - Standard for Type BH Gas Venting Systems.

    - Uniform Mechanical Code.

  - SUBMITTALS

    - Submit under provisions of Section 01 30 00 - Administrative Requirements.

    - Product Data:

      - Layout drawings and sizing calculations if applicable.

      - Manufacturer's data sheets on each product to be used.

      - Preparation instructions and recommendations.

      - Storage and handling requirements and recommendations.

      - Typical installation methods.

      - Product warranty.

** NOTE TO SPECIFIER ** Delete if not applicable to product type.

    - Verification Samples: Two representative units of each type, size, pattern, and color.

    - Shop Drawings: Include details of materials, construction, and finish. Include relationship with adjacent construction.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: Company specializing in manufacturing products specified in this section with a minimum five years documented experience.

    - Installer Qualifications: Company specializing in performing Work of this section with minimum two years documented experience with projects of similar scope and complexity.

    - Source Limitations: Provide each type of product from a single manufacturing source to ensure uniformity.

** NOTE TO SPECIFIER ** Include mock-up if the project size or quality warrant the expense. The following is one example of how a mock-up on might be specified. When deciding on the extent of the mock-up, consider all the major different types of work on the project.

    - Mock-Up: Construct a mock-up with actual materials in sufficient time for Architect's review and to not delay construction progress. Locate mock-up as acceptable to Architect and provide temporary foundations and support.

      - Intent of mock-up is to demonstrate quality of workmanship and visual appearance.

      - If mock-up is not acceptable, rebuild mock-up until satisfactory results are achieved.

      - Retain mock-up during construction as a standard for comparison with completed work.

      - Do not alter or remove mock-up until work is completed or removal is authorized.

  - PRE-INSTALLATION CONFERENCE

    - Convene a conference approximately two weeks before scheduled commencement of the Work. Attendees shall include Architect, Contractor and trades involved. Agenda shall include schedule, responsibilities, critical path items and approvals.

  - DELIVERY, STORAGE, AND HANDLING

    - Store and handle in strict compliance with manufacturer's written instructions and recommendations.

    - Protect from damage due to weather, excessive temperature, and construction operations.

  - PROJECT CONDITIONS

    - Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's recommended limits.

  - WARRANTY

    - Manufacturer's standard limited warranty unless indicated otherwise.

      - The manufacturer shall warrant the Vent System against defects in material and workmanship for a period of 15 years from the date of the purchase. Any portion of the vent repaired or replaced under the warranty shall be warranted for the remainder of the original warranty period.

- PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer: Z-Flex U.S. Inc., which is located at:<BR />20 Commerce Park N.<BR />Bedford, NH null<BR />Toll Free Tel: 800-654-5600<BR />Tel: 603-669-5136<BR />Fax: 603-669-0309<BR />Email: request info (mcreonte@z-flex.com);Web: https://www.z-flex.com | https://www.novaflexgroup.com

** NOTE TO SPECIFIER ** Delete one of the following two paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

    - Substitutions: Not permitted.

    - Requests for substitutions will be considered in accordance with provisions of Section 01 60 00 - Product Requirements.

** NOTE TO SPECIFIER ** Delete article not required.

  - LISTED SINGLE WALL STAINLESS STEEL VENT

    - Listed Single Wall Stainless Steel Vent for Category I, II, III, IV Gas Fired Appliances.

      - Basis of Design: Z-Vent Single Wall manufactured by Z-Flex U.S. or Flexmaster Canada.

      - Codes and Applicable Standards Compliance:

        - Listed to UL1738 Vent Standards.

        - Listed to ULC-S636 Vent Standards.

        - Installed in accordance with all applicable local, state, and national and provincial codes, ordinances, regulations, and laws such as:

          - National Fuel Gas Code.

          - ANSI Z223.1/NFPA-54 (USA).

          - Natural Gas and Propane Installation Code, B149.1 (Canada)

          - BOCA National Mechanical Code.

          - Standard Mechanical Code.

          - Uniform Mechanical Code where applicable.

      - Factory built single wall vent engineered for use with category I, II, III or IV gas fired appliances or as specified by the gas fired appliance manufacturer.

      - Constructed of UL Listed UNS S44735 (i.e. AL 29-4C) superferritic stainless steel or UL listed alternate.

      - Vents include factory installed Double Fail Safe FKM (fluoroelastomer) gasket in the female end of vent yielding an air and water tight joint when the overlapping male/female ends are assembled per the vent manufacturer's instructions.

      - Single wall vent to be compatible to double wall and Smoothcore flexible vents with an adaptor all from the same vent manufacturer.

      - Maximum UL rated vent gas temperature:

        - For vents up to 12 inch (305 mm) diameter: 550 degrees F (288 degrees C)

        - For vents 14 to 24 inch (356 to 610 mm) diameter: 480 degrees F (249 degrees C)

      - Vent to be UL rated for a maximum pressure of 8 inches (203 mm) w.c. and pass the UL leakage test at 20 inches (508 mm) w.c.

      - The vent system is to be continuous from the appliance's flue outlet to the vent termination outside the building.

        - Systems components such as vent supports, roof or wall penetrations, terminations, connectors and drain fittings shall be UL/cUL listed and supplied by the same vent manufacturer.

      - Vent components in direct contact with products of combustion must include a UL/cUL label.

** NOTE TO SPECIFIER ** Delete article not required.

  - LISTED DOUBLE WALL STAINLESS STEEL VENT

    - Listed Double Wall Stainless Steel Vent for Category I, II, III, IV Gas Fired Appliances.

      - Basis of Design: Z-Vent Double Wall manufactured by Z-Flex U.S. or Flexmaster Canada.

      - Codes and Applicable Standards Compliance:

        - Listed to UL1738 Vent Standards.

        - Listed to ULC-S636 Vent Standards.

        - Installed in accordance with all applicable local, state, and national and provincial codes, ordinances, regulations, and laws such as:

          - National Fuel Gas Code.

          - ANSI Z223.1/NFPA-54 (USA).

          - Natural Gas and Propane Installation Code, B149.1 (Canada)

          - BOCA National Mechanical Code.

          - Standard Mechanical Code.

          - Uniform Mechanical Code where applicable.

      - Factory built double wall vent engineered for use with category I, II, III or IV gas fired appliances or as specified by the gas fired appliance manufacturer.

      - Inner vent shall be constructed of UL Listed UNS S44735 (i.e. AL 29-4C) superferritic stainless steel or UL listed alternate.

      - Inner vent shall include factory installed Double Fail Safe FKM (fluoroelastomer) gasket in the female end of vent yielding an air and water tight joint when the overlapping male/female ends are assembled per the vent manufacturer's instructions.

      - The outer double wall shall be constructed of 304 or 316 stainless steel and have a 1 inch (25 mm) insulating airspace around the inner vent to outer double wall.

      - The outer double wall shall incorporate a joint closure system which includes a snap lock or flanges with ZV-Clamp.

      - Double wall vent to be compatible to double wall and smoothcore flexible vents with an adaptor all from the same vent manufacturer.

      - Maximum UL rated vent gas temperature:

        - For vents up to 12 inch (305 mm) diameter: 550 degrees F (288 degrees C).

        - For vents 14 to 24 inch (356 to 610 mm) diameter: 480 degrees F (249 degrees C).

      - Vent to be UL rated for a maximum pressure of 8 inches (203 mm) w.c. and pass the UL leakage test at 20 inches (508 mm) w.c.

      - The vent system is to be continuous from the appliance's flue outlet to the vent termination outside the building.

        - Systems components such as vent supports, roof or wall penetrations, terminations, connectors and drain fittings shall be UL/cUL listed and supplied by the same vent manufacturer.

      - Vent components in direct contact with products of combustion must include a UL/cUL label.

** NOTE TO SPECIFIER ** Delete article not required.

  - LISTED SMOOTHCORE FLEXIBLE STAINLESS STEEL LINER

    - Listed Smoothcore Flexible Stainless Steel Liner for Category I, II, III, IV Gas Fired Appliances.

      - Basis of Design: Z-Vent Smoothcore manufactured by Z-Flex U.S. or Flexmaster Canada.

      - Codes and Applicable Standards Compliance:

        - Listed to UL1738 Vent Standards.

        - Listed to ULC-S636 Vent Standards.

        - Installed in accordance with all applicable local, state, and national and provincial codes, ordinances, regulations, and laws such as:

          - National Fuel Gas Code.

          - ANSI Z223.1/NFPA-54 (USA).

          - Natural Gas and Propane Installation Code, B149.1 (Canada)

          - BOCA National Mechanical Code.

          - Standard Mechanical Code.

          - Uniform Mechanical Code where applicable.

      - Factory built smoothcore flexible liner shall be engineered for use with category I, II, III or IV gas fired appliances or as specified by the gas fired appliance manufacturer.

      - Flexible liner to be constructed from a single wall overlapped, superferritic stainless steel with a minimum wall thickness of 0.01 inch (0.25 mm) for 4 to 12 inch (102 to 305 mm) vent diameters.

      - Female connector includes a factory installed Double Fail Safe fluoroelastomer (FKM) gasket in the female end of connector yielding an air and water tight joint when the overlapping male/female ends are assembled per the vent manufacturer's instructions.

      - Male end shall be compatible to single wall Z-Vent tees or 90 degree elbows, and double wall Z-Vent with an adaptor all from the same vent manufacturer.

      - Maximum UL rated vent gas temperature:

        - For vents 4 to 12 inch (102 to 305 mm) diameter: 550 degrees F (288 degrees C).

      - Liner shall be UL rated for a maximum pressure of 8 inch (203 mm) w.c. and shall have passed UL leakage test at 20 inch (508 mm) w.c.

      - The vent system shall be continuous from the appliance's flue outlet to the vent termination outside the building.

        - All systems components such as vent supports, roof or wall penetrations, terminations, connectors and drain fittings shall be UL/cUL listed and supplied by the same vent manufacturer.

      - Vent components in direct contact with products of combustion must include a UL/cUL label.

- EXECUTION

  - EXAMINATION

    - Do not begin installation until the substrates have been properly constructed and prepared.

    - If substrate preparation is the responsibility of another installer, notify Architect in writing of unsatisfactory preparation before proceeding.

  - PREPARATION

    - Clean surfaces thoroughly prior to installation.

    - Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

  - INSTALLATION

    - Install in accordance with manufacturer's instructions, approved submittals, and in proper relationship with adjacent construction.

      - Vent System Layout:

        - Vent System and Breachings: Clean, inspect and repair if necessary before connecting to appliance.

        - Maintain air space clearances to combustibles as specified by the manufacturer.

        - Design and install in compliance with manufacturer's installation instructions including vent category, vent diameter, maximum equivalent length and/or allowable vent pressures, number of elbows, condensate drains, terminations, slope, clearances, support, etc.

        - Conform to manufacturer's installation instructions, its UL/cUL listing and state/local codes.

      - Mechanical Equipment:

        - Support any dampers or fans installed in the vent system to prevent any twisting or movement of vent system from fan torque or vibration.

  - CLEANING AND PROTECTION

    - Clean products in accordance with the manufacturers recommendations.

    - Repair or replace damaged products before Substantial Completion.

END OF SECTION